## Table of Contents
Name | Type | Dim | Count | Explanatory text
c | set | 1 | 2 | pump class
Charge | variable | 2 | 768 | Niveau de charge au noeud (n) Ã (t)
Charge_j | equation | 2 | 360 | Niveau de charge aux jonctions (j) Ã (t)
Charge_r | equation | 2 | 384 | Niveau de charge au rÃ©servoir (r) Ã (t)
Charge_s | equation | 4 | 144 | Niveau de charge Ã la source Ã (t)
d | set | 1 | 4 | pump number
Debit_s | equation | 1 | 24 | Equilibre des dÃ©bits Ã la source Ã (t)
degree | set | 1 | 3 | polynomial degrees
demand | parameter | 2 | 371 | demand in water at each reservoir and each hour (m^3.h^-1)
dp | parameter | 1 | 0 | Aliased with d
Elec_pompe | equation | 3 | 144 | Consommation Ã©lectrique de la pompe (k) Ã (t)
gamma | parameter | 2 | 4 | linear fit of the electrical power (kW) on the flow (m^3.h^-1) for each class of pumps
height | parameter | 1 | 32 | elevation at each node relative to s (m)
height0 | parameter | 0 | 1 | reference height at the source (m)
j | set | 1 | 15 | junctions
k | set | 2 | 6 | pumps
kp | set | 2 | 0 | Aliased with k
l | set | 2 | 31 | pipes
n | set | 1 | 32 | nodes
night | set | 1 | 8 | night periods
Noeud | equation | 2 | 360 | Contrainte dÃ©bit noeud (n) Ã (t)
np | equation | 1 | 0 | Aliased with n
obj | equation | 0 | 1 | Objectif
Ordre_pompe | equation | 3 | 144 | Les pompes s allument dans l ordre
Perte_charge | equation | 3 | 744 | Perte charge (n n) Ã (t)
phi | parameter | 3 | 62 | quadratic fit of the pressure loss (m) on the flow (m^3.h^-1) for each pipe
Ppompe | variable | 3 | 144 | Puissance Ã©lectrique de la pompe (k) Ã (t) en (kW)
psi | parameter | 2 | 4 | quadratic fit of the service pressure (m) on the flow (m^3.h^-1) for each class of pumps
Qmax | parameter | 2 | 6 | DÃ©bit maximum
Qmin | parameter | 2 | 6 | DÃ©bit minimum
Qpipe | variable | 3 | 744 | DÃ©bit dans le tuyau (l) Ã (t)
Qpompe | variable | 3 | 144 | DÃ©bit de la pompe (k) Ã (t)
Qpompe_inf | equation | 3 | 144 | Borne infÃ©rieur pompe (k) Ã (t)
Qpompe_sup | equation | 3 | 144 | Borne supÃ©rieur pompe (k) Ã (t)
r | set | 1 | 16 | reservoirs
Satisfaction_demande | equation | 2 | 384 | Satisfaction de la demande en (r) Ã (t)
Son | variable | 3 | 168 | Statu t de la pompe (k) fonctionne Ã (t)
surface | parameter | 1 | 16 | mean surface of each reservoir (m^2)
t | set | 1 | 24 | 1-hour periods
tariff | parameter | 1 | 24 | electricity tariff
tariffday | parameter | 0 | 1 | electricity hourly tariff at day (euro.kWh^-1)
tariffnight | parameter | 0 | 1 | electricity hourly tariff at night (euro.kWh^-1)
v | variable | 2 | 384 | Volume au rÃ©servoir (r) en (t)
vinit | parameter | 2 | 16 | initial volume of each reservoir
vmax | parameter | 1 | 16 | maximal volume of each reservoir (m^3)
vmin | parameter | 1 | 16 | minimal volume of each reservoir (m^3)
z | variable | 0 | 1 | CoÃ»t exploitation final

## comments
Commentaires
Pompe large fixées à 1, Volume max augmenté de 10%. Tolérance relative à 0,1, borne inférieure à 499. Temps de calcul : 6 secondes.

## Scalar
TOC
Parameter | Value | Explanatory text
height0 | 0 | reference height at the source (m)
tariffday | 0.04609 | electricity hourly tariff at day (euro.kWh^-1)
tariffnight | 0.02916 | electricity hourly tariff at night (euro.kWh^-1)
Variable | Lowerbound | Value | Upperbound | Marginal | Explanatory text
z | -INF | 502.4944 | INF | 0 | CoÃ»t exploitation final
Equation | Lowerbound | Value | Upperbound | Marginal | Explanatory text
obj | 0 | 0 | 0 | 1 | Objectif

## c
TOC
c | (set) | pump class
dim1
small
large

## Charge
TOC
Charge | (variable) | Niveau de charge au noeud (n) Ã (t)
n | t | Lowerbound | Value | Upperbound | Marginal
s | t1 | 0 | 152.0481 | INF | 0
s | t2 | 0 | 152.0475 | INF | 0
s | t3 | 0 | 152.0473 | INF | 0
s | t4 | 0 | 152.0473 | INF | 0
s | t5 | 0 | 152.0472 | INF | 0
s | t6 | 0 | 152.0521 | INF | 0
s | t7 | 0 | 152.0633 | INF | 0
s | t8 | 0 | 152.0795 | INF | 0
s | t9 | 0 | 145.8402 | INF | 0
s | t10 | 0 | 147.1323 | INF | 0
s | t11 | 0 | 151.1433 | INF | 0
s | t12 | 0 | 151.1258 | INF | 0
s | t13 | 0 | 151.1064 | INF | 0
s | t14 | 0 | 151.0916 | INF | 0
s | t15 | 0 | 151.0778 | INF | 0
s | t16 | 0 | 151.0658 | INF | 0
s | t17 | 0 | 151.0538 | INF | 0
s | t18 | 0 | 151.0478 | INF | 0
s | t19 | 0 | 151.0369 | INF | 0
s | t20 | 0 | 151.0295 | INF | 0
s | t21 | 0 | 151.0219 | INF | 0
s | t22 | 0 | 151.0357 | INF | 0
s | t23 | 0 | 151.0318 | INF | 0
s | t24 | 0 | 151.0255 | INF | 0
j39 | t1 | 0 | 149.187 | INF | 0
j39 | t2 | 0 | 149.1802 | INF | 0
j39 | t3 | 0 | 149.1779 | INF | 0
j39 | t4 | 0 | 149.177 | INF | 0
j39 | t5 | 0 | 149.176 | INF | 0
j39 | t6 | 0 | 149.2323 | INF | 0
j39 | t7 | 0 | 149.3589 | INF | 0
j39 | t8 | 0 | 149.5437 | INF | 0
j39 | t9 | 0 | 145.4495 | INF | 0
j39 | t10 | 0 | 146.1901 | INF | 0
j39 | t11 | 0 | 149.5515 | INF | 0
j39 | t12 | 0 | 149.5103 | INF | 0
j39 | t13 | 0 | 149.4648 | INF | 0
j39 | t14 | 0 | 149.4302 | INF | 0
j39 | t15 | 0 | 149.3977 | INF | 0
j39 | t16 | 0 | 149.3695 | INF | 0
j39 | t17 | 0 | 149.3413 | INF | 0
j39 | t18 | 0 | 149.3272 | INF | 0
j39 | t19 | 0 | 149.3016 | INF | 0
j39 | t20 | 0 | 149.2843 | INF | 0
j39 | t21 | 0 | 149.2664 | INF | 0
j39 | t22 | 0 | 149.2988 | INF | 0
j39 | t23 | 0 | 149.2897 | INF | 0
j39 | t24 | 0 | 149.2748 | INF | 0
j14 | t1 | 0 | 146.6043 | INF | 0
j14 | t2 | 0 | 146.592 | INF | 0
j14 | t3 | 0 | 146.5878 | INF | 0
j14 | t4 | 0 | 146.5862 | INF | 0
j14 | t5 | 0 | 146.5843 | INF | 0
j14 | t6 | 0 | 146.687 | INF | 0
j14 | t7 | 0 | 146.9179 | INF | 0
j14 | t8 | 0 | 147.2547 | INF | 0
j14 | t9 | 0 | 145.0159 | INF | 0
j14 | t10 | 0 | 144.8735 | INF | 0
j14 | t11 | 0 | 147.1288 | INF | 0
j14 | t12 | 0 | 147.0517 | INF | 0
j14 | t13 | 0 | 146.9664 | INF | 0
j14 | t14 | 0 | 146.9014 | INF | 0
j14 | t15 | 0 | 146.8405 | INF | 0
j14 | t16 | 0 | 146.7878 | INF | 0
j14 | t17 | 0 | 146.735 | INF | 0
j14 | t18 | 0 | 146.7086 | INF | 0
j14 | t19 | 0 | 146.6606 | INF | 0
j14 | t20 | 0 | 146.6281 | INF | 0
j14 | t21 | 0 | 146.5945 | INF | 0
j14 | t22 | 0 | 146.6553 | INF | 0
j14 | t23 | 0 | 146.6383 | INF | 0
j14 | t24 | 0 | 146.6104 | INF | 0
j16 | t1 | 0 | 144.6169 | INF | 0
j16 | t2 | 0 | 144.6003 | INF | 0
j16 | t3 | 0 | 144.5946 | INF | 0
j16 | t4 | 0 | 144.5924 | INF | 0
j16 | t5 | 0 | 144.5898 | INF | 0
j16 | t6 | 0 | 144.7282 | INF | 0
j16 | t7 | 0 | 145.0393 | INF | 0
j16 | t8 | 0 | 145.4933 | INF | 0
j16 | t9 | 0 | 144.6598 | INF | 0
j16 | t10 | 0 | 143.8329 | INF | 0
j16 | t11 | 0 | 145.2007 | INF | 0
j16 | t12 | 0 | 145.0949 | INF | 0
j16 | t13 | 0 | 144.978 | INF | 0
j16 | t14 | 0 | 144.8889 | INF | 0
j16 | t15 | 0 | 144.8054 | INF | 0
j16 | t16 | 0 | 144.733 | INF | 0
j16 | t17 | 0 | 144.6607 | INF | 0
j16 | t18 | 0 | 144.6245 | INF | 0
j16 | t19 | 0 | 144.5586 | INF | 0
j16 | t20 | 0 | 144.5141 | INF | 0
j16 | t21 | 0 | 144.468 | INF | 0
j16 | t22 | 0 | 144.5513 | INF | 0
j16 | t23 | 0 | 144.5281 | INF | 0
j16 | t24 | 0 | 144.4898 | INF | 0
j17 | t1 | 0 | 143.1823 | INF | 0
j17 | t2 | 0 | 143.1627 | INF | 0
j17 | t3 | 0 | 143.1559 | INF | 0
j17 | t4 | 0 | 143.1534 | INF | 0
j17 | t5 | 0 | 143.1502 | INF | 0
j17 | t6 | 0 | 143.3145 | INF | 0
j17 | t7 | 0 | 143.6835 | INF | 0
j17 | t8 | 0 | 144.222 | INF | 0
j17 | t9 | 0 | 143.9272 | INF | 0
j17 | t10 | 0 | 143.0442 | INF | 0
j17 | t11 | 0 | 144.134 | INF | 0
j17 | t12 | 0 | 144.0126 | INF | 0
j17 | t13 | 0 | 143.8784 | INF | 0
j17 | t14 | 0 | 143.7761 | INF | 0
j17 | t15 | 0 | 143.6802 | INF | 0
j17 | t16 | 0 | 143.5972 | INF | 0
j17 | t17 | 0 | 143.5141 | INF | 0
j17 | t18 | 0 | 143.4725 | INF | 0
j17 | t19 | 0 | 143.3969 | INF | 0
j17 | t20 | 0 | 143.3458 | INF | 0
j17 | t21 | 0 | 143.2929 | INF | 0
j17 | t22 | 0 | 143.3886 | INF | 0
j17 | t23 | 0 | 143.3619 | INF | 0
j17 | t24 | 0 | 143.3179 | INF | 0
j19 | t1 | 0 | 139.6265 | INF | 0
j19 | t2 | 0 | 139.5992 | INF | 0
j19 | t3 | 0 | 139.5898 | INF | 0
j19 | t4 | 0 | 139.5863 | INF | 0
j19 | t5 | 0 | 139.5819 | INF | 0
j19 | t6 | 0 | 139.81 | INF | 0
j19 | t7 | 0 | 140.3227 | INF | 0
j19 | t8 | 0 | 141.0706 | INF | 0
j19 | t9 | 0 | 141.9053 | INF | 0
j19 | t10 | 0 | 140.8646 | INF | 0
j19 | t11 | 0 | 141.1711 | INF | 0
j19 | t12 | 0 | 141.0054 | INF | 0
j19 | t13 | 0 | 140.8223 | INF | 0
j19 | t14 | 0 | 140.6829 | INF | 0
j19 | t15 | 0 | 140.5521 | INF | 0
j19 | t16 | 0 | 140.4388 | INF | 0
j19 | t17 | 0 | 140.3254 | INF | 0
j19 | t18 | 0 | 140.2688 | INF | 0
j19 | t19 | 0 | 140.1656 | INF | 0
j19 | t20 | 0 | 140.0959 | INF | 0
j19 | t21 | 0 | 140.0237 | INF | 0
j19 | t22 | 0 | 140.1542 | INF | 0
j19 | t23 | 0 | 140.1178 | INF | 0
j19 | t24 | 0 | 140.0578 | INF | 0
j21 | t1 | 0 | 136.1662 | INF | 0
j21 | t2 | 0 | 136.1314 | INF | 0
j21 | t3 | 0 | 136.1195 | INF | 0
j21 | t4 | 0 | 136.115 | INF | 0
j21 | t5 | 0 | 136.1095 | INF | 0
j21 | t6 | 0 | 136.3997 | INF | 0
j21 | t7 | 0 | 137.0522 | INF | 0
j21 | t8 | 0 | 137.9678 | INF | 0
j21 | t9 | 0 | 138.4581 | INF | 0
j21 | t10 | 0 | 138.0254 | INF | 0
j21 | t11 | 0 | 137.6313 | INF | 0
j21 | t12 | 0 | 137.4131 | INF | 0
j21 | t13 | 0 | 137.1718 | INF | 0
j21 | t14 | 0 | 136.9881 | INF | 0
j21 | t15 | 0 | 136.8158 | INF | 0
j21 | t16 | 0 | 136.6664 | INF | 0
j21 | t17 | 0 | 136.5171 | INF | 0
j21 | t18 | 0 | 136.4425 | INF | 0
j21 | t19 | 0 | 136.3066 | INF | 0
j21 | t20 | 0 | 136.2147 | INF | 0
j21 | t21 | 0 | 136.1196 | INF | 0
j21 | t22 | 0 | 136.2916 | INF | 0
j21 | t23 | 0 | 136.2436 | INF | 0
j21 | t24 | 0 | 136.1646 | INF | 0
j24 | t1 | 0 | 144.6014 | INF | 0
j24 | t2 | 0 | 144.5848 | INF | 0
j24 | t3 | 0 | 144.5791 | INF | 0
j24 | t4 | 0 | 144.5769 | INF | 0
j24 | t5 | 0 | 144.5743 | INF | 0
j24 | t6 | 0 | 144.713 | INF | 0
j24 | t7 | 0 | 145.0247 | INF | 0
j24 | t8 | 0 | 145.4795 | INF | 0
j24 | t9 | 0 | 144.6591 | INF | 0
j24 | t10 | 0 | 143.825 | INF | 0
j24 | t11 | 0 | 145.1827 | INF | 0
j24 | t12 | 0 | 145.0767 | INF | 0
j24 | t13 | 0 | 144.9594 | INF | 0
j24 | t14 | 0 | 144.8701 | INF | 0
j24 | t15 | 0 | 144.7864 | INF | 0
j24 | t16 | 0 | 144.7139 | INF | 0
j24 | t17 | 0 | 144.6413 | INF | 0
j24 | t18 | 0 | 144.605 | INF | 0
j24 | t19 | 0 | 144.539 | INF | 0
j24 | t20 | 0 | 144.4944 | INF | 0
j24 | t21 | 0 | 144.4482 | INF | 0
j24 | t22 | 0 | 144.5317 | INF | 0
j24 | t23 | 0 | 144.5084 | INF | 0
j24 | t24 | 0 | 144.47 | INF | 0
j26 | t1 | 0 | 138.3988 | INF | 0
j26 | t2 | 0 | 138.2711 | INF | 0
j26 | t3 | 0 | 138.2608 | INF | 0
j26 | t4 | 0 | 138.2569 | INF | 0
j26 | t5 | 0 | 139.7663 | INF | 0
j26 | t6 | 0 | 139.5082 | INF | 0
j26 | t7 | 0 | 139.0664 | INF | 0
j26 | t8 | 0 | 140.7029 | INF | 0
j26 | t9 | 0 | 144.385 | INF | 0
j26 | t10 | 0 | 140.8447 | INF | 0
j26 | t11 | 0 | 137.8661 | INF | 0
j26 | t12 | 0 | 137.6517 | INF | 0
j26 | t13 | 0 | 137.4146 | INF | 0
j26 | t14 | 0 | 137.234 | INF | 0
j26 | t15 | 0 | 138.2114 | INF | 0
j26 | t16 | 0 | 136.9179 | INF | 0
j26 | t17 | 0 | 136.7712 | INF | 0
j26 | t18 | 0 | 136.6978 | INF | 0
j26 | t19 | 0 | 136.5643 | INF | 0
j26 | t20 | 0 | 136.474 | INF | 0
j26 | t21 | 0 | 136.3806 | INF | 0
j26 | t22 | 0 | 136.5495 | INF | 0
j26 | t23 | 0 | 136.5024 | INF | 0
j26 | t24 | 0 | 136.6902 | INF | 0
j27 | t1 | 0 | 138.024 | INF | 0
j27 | t2 | 0 | 136.916 | INF | 0
j27 | t3 | 0 | 136.178 | INF | 0
j27 | t4 | 0 | 138.2569 | INF | 0
j27 | t5 | 0 | 139.7489 | INF | 0
j27 | t6 | 0 | 139.5082 | INF | 0
j27 | t7 | 0 | 136.8167 | INF | 0
j27 | t8 | 0 | 140.6435 | INF | 0
j27 | t9 | 0 | 144.3774 | INF | 0
j27 | t10 | 0 | 140.5633 | INF | 0
j27 | t11 | 0 | 137.3689 | INF | 0
j27 | t12 | 0 | 137.6517 | INF | 0
j27 | t13 | 0 | 134.5659 | INF | 0
j27 | t14 | 0 | 136.1473 | INF | 0
j27 | t15 | 0 | 137.8949 | INF | 0
j27 | t16 | 0 | 136.9145 | INF | 0
j27 | t17 | 0 | 133.7996 | INF | 0
j27 | t18 | 0 | 136.6605 | INF | 0
j27 | t19 | 0 | 136.5643 | INF | 0
j27 | t20 | 0 | 133.4457 | INF | 0
j27 | t21 | 0 | 136.3492 | INF | 0
j27 | t22 | 0 | 134.7531 | INF | 0
j27 | t23 | 0 | 135.9555 | INF | 0
j27 | t24 | 0 | 136.0637 | INF | 0
j30 | t1 | 0 | 135.6486 | INF | 0
j30 | t2 | 0 | 137.7541 | INF | 0
j30 | t3 | 0 | 138.2087 | INF | 0
j30 | t4 | 0 | 130.9974 | INF | 0
j30 | t5 | 0 | 135.0498 | INF | 0
j30 | t6 | 0 | 133.5297 | INF | 0
j30 | t7 | 0 | 139.0664 | INF | 0
j30 | t8 | 0 | 136.813 | INF | 0
j30 | t9 | 0 | 144.176 | INF | 0
j30 | t10 | 0 | 139.882 | INF | 0
j30 | t11 | 0 | 134.8863 | INF | 0
j30 | t12 | 0 | 129.1229 | INF | 0
j30 | t13 | 0 | 137.4146 | INF | 0
j30 | t14 | 0 | 135.7927 | INF | 0
j30 | t15 | 0 | 134.8852 | INF | 0
j30 | t16 | 0 | 128.3085 | INF | 0
j30 | t17 | 0 | 136.7712 | INF | 0
j30 | t18 | 0 | 129.2405 | INF | 0
j30 | t19 | 0 | 127.4041 | INF | 0
j30 | t20 | 0 | 136.474 | INF | 0
j30 | t21 | 0 | 128.6044 | INF | 0
j30 | t22 | 0 | 135.992 | INF | 0
j30 | t23 | 0 | 133.2628 | INF | 0
j30 | t24 | 0 | 133.9141 | INF | 0
j2 | t1 | 0 | 145.1123 | INF | 0
j2 | t2 | 0 | 145.0969 | INF | 0
j2 | t3 | 0 | 145.0916 | INF | 0
j2 | t4 | 0 | 145.0896 | INF | 0
j2 | t5 | 0 | 145.0871 | INF | 0
j2 | t6 | 0 | 145.216 | INF | 0
j2 | t7 | 0 | 145.5057 | INF | 0
j2 | t8 | 0 | 145.9284 | INF | 0
j2 | t9 | 0 | 144.9644 | INF | 0
j2 | t10 | 0 | 145.2741 | INF | 0
j2 | t11 | 0 | 148.1619 | INF | 0
j2 | t12 | 0 | 148.1004 | INF | 0
j2 | t13 | 0 | 148.0324 | INF | 0
j2 | t14 | 0 | 147.9807 | INF | 0
j2 | t15 | 0 | 147.9321 | INF | 0
j2 | t16 | 0 | 147.89 | INF | 0
j2 | t17 | 0 | 147.848 | INF | 0
j2 | t18 | 0 | 147.8269 | INF | 0
j2 | t19 | 0 | 147.7887 | INF | 0
j2 | t20 | 0 | 147.7628 | INF | 0
j2 | t21 | 0 | 147.736 | INF | 0
j2 | t22 | 0 | 147.7844 | INF | 0
j2 | t23 | 0 | 147.7709 | INF | 0
j2 | t24 | 0 | 147.7487 | INF | 0
j3 | t1 | 0 | 142.713 | INF | 0
j3 | t2 | 0 | 140.7882 | INF | 0
j3 | t3 | 0 | 116.4278 | INF | 0
j3 | t4 | 0 | 139.6545 | INF | 0
j3 | t5 | 0 | 145.0871 | INF | 0
j3 | t6 | 0 | 145.2159 | INF | 0
j3 | t7 | 0 | 141.2715 | INF | 0
j3 | t8 | 0 | 140.9402 | INF | 0
j3 | t9 | 0 | 144.84 | INF | 0
j3 | t10 | 0 | 144.5091 | INF | 0
j3 | t11 | 0 | 146.9953 | INF | 0
j3 | t12 | 0 | 138.7439 | INF | 0
j3 | t13 | 0 | 148.0324 | INF | 0
j3 | t14 | 0 | 144.4882 | INF | 0
j3 | t15 | 0 | 147.9321 | INF | 0
j3 | t16 | 0 | 147.89 | INF | 0
j3 | t17 | 0 | 128.4457 | INF | 0
j3 | t18 | 0 | 147.8269 | INF | 0
j3 | t19 | 0 | 147.7281 | INF | 0
j3 | t20 | 0 | 147.7628 | INF | 0
j3 | t21 | 0 | 144.281 | INF | 0
j3 | t22 | 0 | 147.7844 | INF | 0
j3 | t23 | 0 | 147.7709 | INF | 0
j3 | t24 | 0 | 145.3265 | INF | 0
j6 | t1 | 0 | 135.1706 | INF | 0
j6 | t2 | 0 | 136.339 | INF | 0
j6 | t3 | 0 | 142.0967 | INF | 0
j6 | t4 | 0 | 136.8794 | INF | 0
j6 | t5 | 0 | 131.176 | INF | 0
j6 | t6 | 0 | 131.5577 | INF | 0
j6 | t7 | 0 | 137.3284 | INF | 0
j6 | t8 | 0 | 138.7455 | INF | 0
j6 | t9 | 0 | 143.612 | INF | 0
j6 | t10 | 0 | 143.1774 | INF | 0
j6 | t11 | 0 | 144.9939 | INF | 0
j6 | t12 | 0 | 146.9914 | INF | 0
j6 | t13 | 0 | 143.1592 | INF | 0
j6 | t14 | 0 | 145.6388 | INF | 0
j6 | t15 | 0 | 142.9461 | INF | 0
j6 | t16 | 0 | 142.8567 | INF | 0
j6 | t17 | 0 | 147.4742 | INF | 0
j6 | t18 | 0 | 142.7227 | INF | 0
j6 | t19 | 0 | 143.0064 | INF | 0
j6 | t20 | 0 | 142.5864 | INF | 0
j6 | t21 | 0 | 145.1914 | INF | 0
j6 | t22 | 0 | 142.6324 | INF | 0
j6 | t23 | 0 | 142.6037 | INF | 0
j6 | t24 | 0 | 144.8397 | INF | 0
j7 | t1 | 0 | 132.4627 | INF | 0
j7 | t2 | 0 | 135.6412 | INF | 0
j7 | t3 | 0 | 137.3937 | INF | 0
j7 | t4 | 0 | 136.3345 | INF | 0
j7 | t5 | 0 | 127.3592 | INF | 0
j7 | t6 | 0 | 128.6641 | INF | 0
j7 | t7 | 0 | 125.2399 | INF | 0
j7 | t8 | 0 | 133.8051 | INF | 0
j7 | t9 | 0 | 142.4938 | INF | 0
j7 | t10 | 0 | 141.5152 | INF | 0
j7 | t11 | 0 | 140.0191 | INF | 0
j7 | t12 | 0 | 145.25 | INF | 0
j7 | t13 | 0 | 138.7398 | INF | 0
j7 | t14 | 0 | 145.1451 | INF | 0
j7 | t15 | 0 | 137.6674 | INF | 0
j7 | t16 | 0 | 142.8567 | INF | 0
j7 | t17 | 0 | 146.9437 | INF | 0
j7 | t18 | 0 | 142.7227 | INF | 0
j7 | t19 | 0 | 140.9036 | INF | 0
j7 | t20 | 0 | 139.6154 | INF | 0
j7 | t21 | 0 | 144.7023 | INF | 0
j7 | t22 | 0 | 139.9314 | INF | 0
j7 | t23 | 0 | 141.6646 | INF | 0
j7 | t24 | 0 | 142.2011 | INF | 0
j10 | t1 | 0 | 121.1486 | INF | 0
j10 | t2 | 0 | 114.7199 | INF | 0
j10 | t3 | 0 | 142.0967 | INF | 0
j10 | t4 | 0 | 115.569 | INF | 0
j10 | t5 | 0 | 111.757 | INF | 0
j10 | t6 | 0 | 109.0738 | INF | 0
j10 | t7 | 0 | 137.2773 | INF | 0
j10 | t8 | 0 | 135.2228 | INF | 0
j10 | t9 | 0 | 143.1221 | INF | 0
j10 | t10 | 0 | 142.366 | INF | 0
j10 | t11 | 0 | 144.9939 | INF | 0
j10 | t12 | 0 | 146.9914 | INF | 0
j10 | t13 | 0 | 141.8979 | INF | 0
j10 | t14 | 0 | 141.6308 | INF | 0
j10 | t15 | 0 | 142.2037 | INF | 0
j10 | t16 | 0 | 122.8583 | INF | 0
j10 | t17 | 0 | 147.4628 | INF | 0
j10 | t18 | 0 | 122.4414 | INF | 0
j10 | t19 | 0 | 138.4979 | INF | 0
j10 | t20 | 0 | 139.1143 | INF | 0
j10 | t21 | 0 | 140.6248 | INF | 0
j10 | t22 | 0 | 138.7095 | INF | 0
j10 | t23 | 0 | 133.2182 | INF | 0
j10 | t24 | 0 | 144.0631 | INF | 0
r12 | t1 | 0 | 144.3125 | INF | 0
r12 | t2 | 0 | 144.2955 | INF | 0
r12 | t3 | 0 | 144.2898 | INF | 0
r12 | t4 | 0 | 144.2875 | INF | 0
r12 | t5 | 0 | 144.2848 | INF | 0
r12 | t6 | 0 | 144.4261 | INF | 0
r12 | t7 | 0 | 144.7437 | INF | 0
r12 | t8 | 0 | 145.2074 | INF | 0
r12 | t9 | 0 | 144.8983 | INF | 0
r12 | t10 | 0 | 144.1033 | INF | 0
r12 | t11 | 0 | 145.9713 | INF | 0
r12 | t12 | 0 | 145.8784 | INF | 0
r12 | t13 | 0 | 145.7758 | INF | 0
r12 | t14 | 0 | 145.6977 | INF | 0
r12 | t15 | 0 | 145.6244 | INF | 0
r12 | t16 | 0 | 145.5609 | INF | 0
r12 | t17 | 0 | 145.4974 | INF | 0
r12 | t18 | 0 | 145.4657 | INF | 0
r12 | t19 | 0 | 145.4079 | INF | 0
r12 | t20 | 0 | 145.3689 | INF | 0
r12 | t21 | 0 | 145.3285 | INF | 0
r12 | t22 | 0 | 145.4016 | INF | 0
r12 | t23 | 0 | 145.3812 | INF | 0
r12 | t24 | 0 | 145.3476 | INF | 0
r13 | t1 | 0 | 137.3642 | INF | 0
r13 | t2 | 0 | 137.3297 | INF | 0
r13 | t3 | 0 | 137.3179 | INF | 0
r13 | t4 | 0 | 137.3134 | INF | 0
r13 | t5 | 0 | 137.3079 | INF | 0
r13 | t6 | 0 | 137.5959 | INF | 0
r13 | t7 | 0 | 138.2425 | INF | 0
r13 | t8 | 0 | 139.1838 | INF | 0
r13 | t9 | 0 | 143.9272 | INF | 0
r13 | t10 | 0 | 143.0442 | INF | 0
r13 | t11 | 0 | 144.134 | INF | 0
r13 | t12 | 0 | 144.0126 | INF | 0
r13 | t13 | 0 | 143.8784 | INF | 0
r13 | t14 | 0 | 143.7761 | INF | 0
r13 | t15 | 0 | 143.6802 | INF | 0
r13 | t16 | 0 | 143.5972 | INF | 0
r13 | t17 | 0 | 143.5141 | INF | 0
r13 | t18 | 0 | 143.4725 | INF | 0
r13 | t19 | 0 | 143.3969 | INF | 0
r13 | t20 | 0 | 143.3458 | INF | 0
r13 | t21 | 0 | 143.2929 | INF | 0
r13 | t22 | 0 | 143.3886 | INF | 0
r13 | t23 | 0 | 143.3619 | INF | 0
r13 | t24 | 0 | 143.3179 | INF | 0
r132 | t1 | 0 | 138.7605 | INF | 0
r132 | t2 | 0 | 138.7314 | INF | 0
r132 | t3 | 0 | 138.7214 | INF | 0
r132 | t4 | 0 | 138.7176 | INF | 0
r132 | t5 | 0 | 138.713 | INF | 0
r132 | t6 | 0 | 138.9558 | INF | 0
r132 | t7 | 0 | 139.5017 | INF | 0
r132 | t8 | 0 | 140.318 | INF | 0
r132 | t9 | 0 | 141.8603 | INF | 0
r132 | t10 | 0 | 140.627 | INF | 0
r132 | t11 | 0 | 140.7455 | INF | 0
r132 | t12 | 0 | 140.5739 | INF | 0
r132 | t13 | 0 | 140.3842 | INF | 0
r132 | t14 | 0 | 140.2397 | INF | 0
r132 | t15 | 0 | 140.1042 | INF | 0
r132 | t16 | 0 | 139.9868 | INF | 0
r132 | t17 | 0 | 139.8694 | INF | 0
r132 | t18 | 0 | 139.8107 | INF | 0
r132 | t19 | 0 | 139.7038 | INF | 0
r132 | t20 | 0 | 139.6315 | INF | 0
r132 | t21 | 0 | 139.5568 | INF | 0
r132 | t22 | 0 | 139.692 | INF | 0
r132 | t23 | 0 | 139.6543 | INF | 0
r132 | t24 | 0 | 139.5921 | INF | 0
r133 | t1 | 0 | 135.4585 | INF | 0
r133 | t2 | 0 | 135.3357 | INF | 0
r133 | t3 | 0 | 135.2821 | INF | 0
r133 | t4 | 0 | 135.2583 | INF | 0
r133 | t5 | 0 | 135.2254 | INF | 0
r133 | t6 | 0 | 135.8427 | INF | 0
r133 | t7 | 0 | 136.7534 | INF | 0
r133 | t8 | 0 | 137.8377 | INF | 0
r133 | t9 | 0 | 138.2879 | INF | 0
r133 | t10 | 0 | 137.6663 | INF | 0
r133 | t11 | 0 | 136.6572 | INF | 0
r133 | t12 | 0 | 136.4245 | INF | 0
r133 | t13 | 0 | 136.1673 | INF | 0
r133 | t14 | 0 | 135.9713 | INF | 0
r133 | t15 | 0 | 135.7876 | INF | 0
r133 | t16 | 0 | 135.6284 | INF | 0
r133 | t17 | 0 | 135.4692 | INF | 0
r133 | t18 | 0 | 135.3895 | INF | 0
r133 | t19 | 0 | 135.2446 | INF | 0
r133 | t20 | 0 | 135.1467 | INF | 0
r133 | t21 | 0 | 135.1706 | INF | 0
r133 | t22 | 0 | 135.6792 | INF | 0
r133 | t23 | 0 | 135.5689 | INF | 0
r133 | t24 | 0 | 135.35 | INF | 0
r134 | t1 | 0 | 136.1 | INF | 0
r134 | t2 | 0 | 136.1 | INF | 0
r134 | t3 | 0 | 136.1 | INF | 0
r134 | t4 | 0 | 136.1 | INF | 0
r134 | t5 | 0 | 136.1 | INF | 0
r134 | t6 | 0 | 136.2424 | INF | 0
r134 | t7 | 0 | 136.5911 | INF | 0
r134 | t8 | 0 | 137.1001 | INF | 0
r134 | t9 | 0 | 137.5959 | INF | 0
r134 | t10 | 0 | 137.7806 | INF | 0
r134 | t11 | 0 | 137.6313 | INF | 0
r134 | t12 | 0 | 137.4131 | INF | 0
r134 | t13 | 0 | 137.1718 | INF | 0
r134 | t14 | 0 | 136.9881 | INF | 0
r134 | t15 | 0 | 136.8158 | INF | 0
r134 | t16 | 0 | 136.6664 | INF | 0
r134 | t17 | 0 | 136.5171 | INF | 0
r134 | t18 | 0 | 136.4425 | INF | 0
r134 | t19 | 0 | 136.3066 | INF | 0
r134 | t20 | 0 | 136.2147 | INF | 0
r134 | t21 | 0 | 136.1 | INF | 0
r134 | t22 | 0 | 136.1 | INF | 0
r134 | t23 | 0 | 136.1 | INF | 0
r134 | t24 | 0 | 136.1 | INF | 0
r14 | t1 | 0 | 144.5998 | INF | 0
r14 | t2 | 0 | 144.5848 | INF | 0
r14 | t3 | 0 | 144.5791 | INF | 0
r14 | t4 | 0 | 144.5769 | INF | 0
r14 | t5 | 0 | 144.3078 | INF | 0
r14 | t6 | 0 | 144.5964 | INF | 0
r14 | t7 | 0 | 145.0247 | INF | 0
r14 | t8 | 0 | 145.3945 | INF | 0
r14 | t9 | 0 | 144.6591 | INF | 0
r14 | t10 | 0 | 143.8133 | INF | 0
r14 | t11 | 0 | 145.1827 | INF | 0
r14 | t12 | 0 | 145.0767 | INF | 0
r14 | t13 | 0 | 144.9594 | INF | 0
r14 | t14 | 0 | 144.8701 | INF | 0
r14 | t15 | 0 | 144.6655 | INF | 0
r14 | t16 | 0 | 144.7139 | INF | 0
r14 | t17 | 0 | 144.6413 | INF | 0
r14 | t18 | 0 | 144.605 | INF | 0
r14 | t19 | 0 | 144.539 | INF | 0
r14 | t20 | 0 | 144.4944 | INF | 0
r14 | t21 | 0 | 144.4482 | INF | 0
r14 | t22 | 0 | 144.5317 | INF | 0
r14 | t23 | 0 | 144.5084 | INF | 0
r14 | t24 | 0 | 144.463 | INF | 0
r15 | t1 | 0 | 135.4298 | INF | 0
r15 | t2 | 0 | 137.2738 | INF | 0
r15 | t3 | 0 | 138.2087 | INF | 0
r15 | t4 | 0 | 130.9974 | INF | 0
r15 | t5 | 0 | 126.7662 | INF | 0
r15 | t6 | 0 | 133.5294 | INF | 0
r15 | t7 | 0 | 139.0664 | INF | 0
r15 | t8 | 0 | 136.6007 | INF | 0
r15 | t9 | 0 | 144.1463 | INF | 0
r15 | t10 | 0 | 139.7717 | INF | 0
r15 | t11 | 0 | 134.8728 | INF | 0
r15 | t12 | 0 | 128.2848 | INF | 0
r15 | t13 | 0 | 137.4146 | INF | 0
r15 | t14 | 0 | 133.9331 | INF | 0
r15 | t15 | 0 | 133.7128 | INF | 0
r15 | t16 | 0 | 128.3085 | INF | 0
r15 | t17 | 0 | 136.7712 | INF | 0
r15 | t18 | 0 | 126.4097 | INF | 0
r15 | t19 | 0 | 127.4041 | INF | 0
r15 | t20 | 0 | 136.474 | INF | 0
r15 | t21 | 0 | 121.9047 | INF | 0
r15 | t22 | 0 | 135.992 | INF | 0
r15 | t23 | 0 | 133.2628 | INF | 0
r15 | t24 | 0 | 133.5808 | INF | 0
r151 | t1 | 0 | 131.6739 | INF | 0
r151 | t2 | 0 | 137.6562 | INF | 0
r151 | t3 | 0 | 138.1108 | INF | 0
r151 | t4 | 0 | 114.6076 | INF | 0
r151 | t5 | 0 | 135.0498 | INF | 0
r151 | t6 | 0 | 120.0855 | INF | 0
r151 | t7 | 0 | 139.0664 | INF | 0
r151 | t8 | 0 | 130.6733 | INF | 0
r151 | t9 | 0 | 143.9225 | INF | 0
r151 | t10 | 0 | 138.6297 | INF | 0
r151 | t11 | 0 | 128.697 | INF | 0
r151 | t12 | 0 | 117.5428 | INF | 0
r151 | t13 | 0 | 137.4146 | INF | 0
r151 | t14 | 0 | 135.7121 | INF | 0
r151 | t15 | 0 | 132.4833 | INF | 0
r151 | t16 | 0 | 108.8399 | INF | 0
r151 | t17 | 0 | 136.7712 | INF | 0
r151 | t18 | 0 | 124.1865 | INF | 0
r151 | t19 | 0 | 106.6785 | INF | 0
r151 | t20 | 0 | 136.474 | INF | 0
r151 | t21 | 0 | 126.886 | INF | 0
r151 | t22 | 0 | 134.794 | INF | 0
r151 | t23 | 0 | 126.0193 | INF | 0
r151 | t24 | 0 | 130.3727 | INF | 0
r16 | t1 | 0 | 138.0226 | INF | 0
r16 | t2 | 0 | 136.9148 | INF | 0
r16 | t3 | 0 | 136.1762 | INF | 0
r16 | t4 | 0 | 138.2569 | INF | 0
r16 | t5 | 0 | 139.748 | INF | 0
r16 | t6 | 0 | 139.5082 | INF | 0
r16 | t7 | 0 | 136.8046 | INF | 0
r16 | t8 | 0 | 140.6434 | INF | 0
r16 | t9 | 0 | 144.3773 | INF | 0
r16 | t10 | 0 | 140.5625 | INF | 0
r16 | t11 | 0 | 137.3679 | INF | 0
r16 | t12 | 0 | 137.6517 | INF | 0
r16 | t13 | 0 | 134.5631 | INF | 0
r16 | t14 | 0 | 136.1473 | INF | 0
r16 | t15 | 0 | 137.8949 | INF | 0
r16 | t16 | 0 | 136.9145 | INF | 0
r16 | t17 | 0 | 133.7963 | INF | 0
r16 | t18 | 0 | 136.6583 | INF | 0
r16 | t19 | 0 | 136.5643 | INF | 0
r16 | t20 | 0 | 133.4356 | INF | 0
r16 | t21 | 0 | 136.3492 | INF | 0
r16 | t22 | 0 | 134.7531 | INF | 0
r16 | t23 | 0 | 135.9539 | INF | 0
r16 | t24 | 0 | 136.0623 | INF | 0
r161 | t1 | 0 | 134.5561 | INF | 0
r161 | t2 | 0 | 120.3119 | INF | 0
r161 | t3 | 0 | 110.5604 | INF | 0
r161 | t4 | 0 | 138.2569 | INF | 0
r161 | t5 | 0 | 139.7452 | INF | 0
r161 | t6 | 0 | 139.5082 | INF | 0
r161 | t7 | 0 | 119.1419 | INF | 0
r161 | t8 | 0 | 139.9557 | INF | 0
r161 | t9 | 0 | 144.3327 | INF | 0
r161 | t10 | 0 | 137.7217 | INF | 0
r161 | t11 | 0 | 131.8832 | INF | 0
r161 | t12 | 0 | 137.6517 | INF | 0
r161 | t13 | 0 | 100.161 | INF | 0
r161 | t14 | 0 | 119.7453 | INF | 0
r161 | t15 | 0 | 133.2319 | INF | 0
r161 | t16 | 0 | 136.8782 | INF | 0
r161 | t17 | 0 | 98.6363 | INF | 0
r161 | t18 | 0 | 136.6605 | INF | 0
r161 | t19 | 0 | 136.5643 | INF | 0
r161 | t20 | 0 | 105.3063 | INF | 0
r161 | t21 | 0 | 135.9325 | INF | 0
r161 | t22 | 0 | 107.4651 | INF | 0
r161 | t23 | 0 | 130.5332 | INF | 0
r161 | t24 | 0 | 129.446 | INF | 0
r17 | t1 | 0 | 142.6089 | INF | 0
r17 | t2 | 0 | 140.7882 | INF | 0
r17 | t3 | 0 | 115.545 | INF | 0
r17 | t4 | 0 | 139.6474 | INF | 0
r17 | t5 | 0 | 145.0871 | INF | 0
r17 | t6 | 0 | 145.2159 | INF | 0
r17 | t7 | 0 | 141.2715 | INF | 0
r17 | t8 | 0 | 140.8282 | INF | 0
r17 | t9 | 0 | 144.838 | INF | 0
r17 | t10 | 0 | 144.4972 | INF | 0
r17 | t11 | 0 | 146.9233 | INF | 0
r17 | t12 | 0 | 138.6608 | INF | 0
r17 | t13 | 0 | 148.0324 | INF | 0
r17 | t14 | 0 | 144.3917 | INF | 0
r17 | t15 | 0 | 147.9321 | INF | 0
r17 | t16 | 0 | 147.89 | INF | 0
r17 | t17 | 0 | 127.2757 | INF | 0
r17 | t18 | 0 | 147.8269 | INF | 0
r17 | t19 | 0 | 147.7264 | INF | 0
r17 | t20 | 0 | 147.7628 | INF | 0
r17 | t21 | 0 | 144.0704 | INF | 0
r17 | t22 | 0 | 147.7844 | INF | 0
r17 | t23 | 0 | 147.7709 | INF | 0
r17 | t24 | 0 | 145.2689 | INF | 0
r171 | t1 | 0 | 141.7129 | INF | 0
r171 | t2 | 0 | 83.5087 | INF | 0
r171 | t3 | 0 | 84.1062 | INF | 0
r171 | t4 | 0 | 84.8465 | INF | 0
r171 | t5 | 0 | 145.0871 | INF | 0
r171 | t6 | 0 | 145.2159 | INF | 0
r171 | t7 | 0 | 85.5047 | INF | 0
r171 | t8 | 0 | 129.9141 | INF | 0
r171 | t9 | 0 | 144.2411 | INF | 0
r171 | t10 | 0 | 141.5477 | INF | 0
r171 | t11 | 0 | 146.9953 | INF | 0
r171 | t12 | 0 | 89.4403 | INF | 0
r171 | t13 | 0 | 148.0324 | INF | 0
r171 | t14 | 0 | 138.9668 | INF | 0
r171 | t15 | 0 | 147.9321 | INF | 0
r171 | t16 | 0 | 147.89 | INF | 0
r171 | t17 | 0 | 128.4457 | INF | 0
r171 | t18 | 0 | 147.8269 | INF | 0
r171 | t19 | 0 | 147.5524 | INF | 0
r171 | t20 | 0 | 147.7628 | INF | 0
r171 | t21 | 0 | 144.281 | INF | 0
r171 | t22 | 0 | 147.7844 | INF | 0
r171 | t23 | 0 | 147.7709 | INF | 0
r171 | t24 | 0 | 140.2167 | INF | 0
r18 | t1 | 0 | 119.5508 | INF | 0
r18 | t2 | 0 | 114.4269 | INF | 0
r18 | t3 | 0 | 142.0967 | INF | 0
r18 | t4 | 0 | 115.569 | INF | 0
r18 | t5 | 0 | 90.4545 | INF | 0
r18 | t6 | 0 | 91.5015 | INF | 0
r18 | t7 | 0 | 136.9443 | INF | 0
r18 | t8 | 0 | 134.7167 | INF | 0
r18 | t9 | 0 | 142.4496 | INF | 0
r18 | t10 | 0 | 140.0193 | INF | 0
r18 | t11 | 0 | 144.9939 | INF | 0
r18 | t12 | 0 | 146.9914 | INF | 0
r18 | t13 | 0 | 141.8979 | INF | 0
r18 | t14 | 0 | 137.9842 | INF | 0
r18 | t15 | 0 | 133.4571 | INF | 0
r18 | t16 | 0 | 122.8583 | INF | 0
r18 | t17 | 0 | 147.4628 | INF | 0
r18 | t18 | 0 | 122.4414 | INF | 0
r18 | t19 | 0 | 138.4979 | INF | 0
r18 | t20 | 0 | 96.0525 | INF | 0
r18 | t21 | 0 | 140.6248 | INF | 0
r18 | t22 | 0 | 138.7095 | INF | 0
r18 | t23 | 0 | 133.2182 | INF | 0
r18 | t24 | 0 | 144.0631 | INF | 0
r181 | t1 | 0 | 110.73 | INF | 0
r181 | t2 | 0 | 96.4305 | INF | 0
r181 | t3 | 0 | 142.0967 | INF | 0
r181 | t4 | 0 | 96.4886 | INF | 0
r181 | t5 | 0 | 102.9148 | INF | 0
r181 | t6 | 0 | 97.4917 | INF | 0
r181 | t7 | 0 | 137.2737 | INF | 0
r181 | t8 | 0 | 132.6632 | INF | 0
r181 | t9 | 0 | 142.916 | INF | 0
r181 | t10 | 0 | 142.1572 | INF | 0
r181 | t11 | 0 | 144.9939 | INF | 0
r181 | t12 | 0 | 146.9914 | INF | 0
r181 | t13 | 0 | 140.7909 | INF | 0
r181 | t14 | 0 | 139.6611 | INF | 0
r181 | t15 | 0 | 142.2037 | INF | 0
r181 | t16 | 0 | 104.9563 | INF | 0
r181 | t17 | 0 | 147.4542 | INF | 0
r181 | t18 | 0 | 104.2853 | INF | 0
r181 | t19 | 0 | 134.4922 | INF | 0
r181 | t20 | 0 | 139.1143 | INF | 0
r181 | t21 | 0 | 136.5671 | INF | 0
r181 | t22 | 0 | 135.2275 | INF | 0
r181 | t23 | 0 | 124.843 | INF | 0
r181 | t24 | 0 | 143.3863 | INF | 0
r19 | t1 | 0 | 126.1044 | INF | 0
r19 | t2 | 0 | 127.6961 | INF | 0
r19 | t3 | 0 | 81.5815 | INF | 0
r19 | t4 | 0 | 130.1836 | INF | 0
r19 | t5 | 0 | 82.1948 | INF | 0
r19 | t6 | 0 | 128.6641 | INF | 0
r19 | t7 | 0 | 125.2399 | INF | 0
r19 | t8 | 0 | 116.1013 | INF | 0
r19 | t9 | 0 | 139.2045 | INF | 0
r19 | t10 | 0 | 139.9605 | INF | 0
r19 | t11 | 0 | 126.3709 | INF | 0
r19 | t12 | 0 | 129.6962 | INF | 0
r19 | t13 | 0 | 123.4542 | INF | 0
r19 | t14 | 0 | 139.5933 | INF | 0
r19 | t15 | 0 | 137.6674 | INF | 0
r19 | t16 | 0 | 142.8567 | INF | 0
r19 | t17 | 0 | 140.9612 | INF | 0
r19 | t18 | 0 | 142.7227 | INF | 0
r19 | t19 | 0 | 116.2713 | INF | 0
r19 | t20 | 0 | 139.6105 | INF | 0
r19 | t21 | 0 | 139.2035 | INF | 0
r19 | t22 | 0 | 115.0443 | INF | 0
r19 | t23 | 0 | 134.7185 | INF | 0
r19 | t24 | 0 | 130.7921 | INF | 0
r191 | t1 | 0 | 131.1651 | INF | 0
r191 | t2 | 0 | 135.6412 | INF | 0
r191 | t3 | 0 | 137.3937 | INF | 0
r191 | t4 | 0 | 136.3345 | INF | 0
r191 | t5 | 0 | 127.3592 | INF | 0
r191 | t6 | 0 | 124.4543 | INF | 0
r191 | t7 | 0 | 107.6527 | INF | 0
r191 | t8 | 0 | 132.2358 | INF | 0
r191 | t9 | 0 | 142.0402 | INF | 0
r191 | t10 | 0 | 140.1937 | INF | 0
r191 | t11 | 0 | 137.9468 | INF | 0
r191 | t12 | 0 | 145.188 | INF | 0
r191 | t13 | 0 | 137.2749 | INF | 0
r191 | t14 | 0 | 145.1451 | INF | 0
r191 | t15 | 0 | 129.9876 | INF | 0
r191 | t16 | 0 | 142.8567 | INF | 0
r191 | t17 | 0 | 146.9437 | INF | 0
r191 | t18 | 0 | 142.7227 | INF | 0
r191 | t19 | 0 | 140.9036 | INF | 0
r191 | t20 | 0 | 135.3326 | INF | 0
r191 | t21 | 0 | 144.7023 | INF | 0
r191 | t22 | 0 | 139.8534 | INF | 0
r191 | t23 | 0 | 141.5866 | INF | 0
r191 | t24 | 0 | 141.5333 | INF | 0

## Charge_j
TOC
Charge_j | (equation) | Niveau de charge aux jonctions (j) Ã (t)
n | t | Lowerbound | Value | Upperbound | Marginal
j39 | t1 | 68 | 149.187 | INF | 0
j39 | t2 | 68 | 149.1802 | INF | 0
j39 | t3 | 68 | 149.1779 | INF | 0
j39 | t4 | 68 | 149.177 | INF | 0
j39 | t5 | 68 | 149.176 | INF | 0
j39 | t6 | 68 | 149.2323 | INF | 0
j39 | t7 | 68 | 149.3589 | INF | 0
j39 | t8 | 68 | 149.5437 | INF | 0
j39 | t9 | 68 | 145.4495 | INF | 0
j39 | t10 | 68 | 146.1901 | INF | 0
j39 | t11 | 68 | 149.5515 | INF | 0
j39 | t12 | 68 | 149.5103 | INF | 0
j39 | t13 | 68 | 149.4648 | INF | 0
j39 | t14 | 68 | 149.4302 | INF | 0
j39 | t15 | 68 | 149.3977 | INF | 0
j39 | t16 | 68 | 149.3695 | INF | 0
j39 | t17 | 68 | 149.3413 | INF | 0
j39 | t18 | 68 | 149.3272 | INF | 0
j39 | t19 | 68 | 149.3016 | INF | 0
j39 | t20 | 68 | 149.2843 | INF | 0
j39 | t21 | 68 | 149.2664 | INF | 0
j39 | t22 | 68 | 149.2988 | INF | 0
j39 | t23 | 68 | 149.2897 | INF | 0
j39 | t24 | 68 | 149.2748 | INF | 0
j14 | t1 | 63 | 146.6043 | INF | 0
j14 | t2 | 63 | 146.592 | INF | 0
j14 | t3 | 63 | 146.5878 | INF | 0
j14 | t4 | 63 | 146.5862 | INF | 0
j14 | t5 | 63 | 146.5843 | INF | 0
j14 | t6 | 63 | 146.687 | INF | 0
j14 | t7 | 63 | 146.9179 | INF | 0
j14 | t8 | 63 | 147.2547 | INF | 0
j14 | t9 | 63 | 145.0159 | INF | 0
j14 | t10 | 63 | 144.8735 | INF | 0
j14 | t11 | 63 | 147.1288 | INF | 0
j14 | t12 | 63 | 147.0517 | INF | 0
j14 | t13 | 63 | 146.9664 | INF | 0
j14 | t14 | 63 | 146.9014 | INF | 0
j14 | t15 | 63 | 146.8405 | INF | 0
j14 | t16 | 63 | 146.7878 | INF | 0
j14 | t17 | 63 | 146.735 | INF | 0
j14 | t18 | 63 | 146.7086 | INF | 0
j14 | t19 | 63 | 146.6606 | INF | 0
j14 | t20 | 63 | 146.6281 | INF | 0
j14 | t21 | 63 | 146.5945 | INF | 0
j14 | t22 | 63 | 146.6553 | INF | 0
j14 | t23 | 63 | 146.6383 | INF | 0
j14 | t24 | 63 | 146.6104 | INF | 0
j16 | t1 | 87 | 144.6169 | INF | 0
j16 | t2 | 87 | 144.6003 | INF | 0
j16 | t3 | 87 | 144.5946 | INF | 0
j16 | t4 | 87 | 144.5924 | INF | 0
j16 | t5 | 87 | 144.5898 | INF | 0
j16 | t6 | 87 | 144.7282 | INF | 0
j16 | t7 | 87 | 145.0393 | INF | 0
j16 | t8 | 87 | 145.4933 | INF | 0
j16 | t9 | 87 | 144.6598 | INF | 0
j16 | t10 | 87 | 143.8329 | INF | 0
j16 | t11 | 87 | 145.2007 | INF | 0
j16 | t12 | 87 | 145.0949 | INF | 0
j16 | t13 | 87 | 144.978 | INF | 0
j16 | t14 | 87 | 144.8889 | INF | 0
j16 | t15 | 87 | 144.8054 | INF | 0
j16 | t16 | 87 | 144.733 | INF | 0
j16 | t17 | 87 | 144.6607 | INF | 0
j16 | t18 | 87 | 144.6245 | INF | 0
j16 | t19 | 87 | 144.5586 | INF | 0
j16 | t20 | 87 | 144.5141 | INF | 0
j16 | t21 | 87 | 144.468 | INF | 0
j16 | t22 | 87 | 144.5513 | INF | 0
j16 | t23 | 87 | 144.5281 | INF | 0
j16 | t24 | 87 | 144.4898 | INF | 0
j17 | t1 | 99 | 143.1823 | INF | 0
j17 | t2 | 99 | 143.1627 | INF | 0
j17 | t3 | 99 | 143.1559 | INF | 0
j17 | t4 | 99 | 143.1534 | INF | 0
j17 | t5 | 99 | 143.1502 | INF | 0
j17 | t6 | 99 | 143.3145 | INF | 0
j17 | t7 | 99 | 143.6835 | INF | 0
j17 | t8 | 99 | 144.222 | INF | 0
j17 | t9 | 99 | 143.9272 | INF | 0
j17 | t10 | 99 | 143.0442 | INF | 0
j17 | t11 | 99 | 144.134 | INF | 0
j17 | t12 | 99 | 144.0126 | INF | 0
j17 | t13 | 99 | 143.8784 | INF | 0
j17 | t14 | 99 | 143.7761 | INF | 0
j17 | t15 | 99 | 143.6802 | INF | 0
j17 | t16 | 99 | 143.5972 | INF | 0
j17 | t17 | 99 | 143.5141 | INF | 0
j17 | t18 | 99 | 143.4725 | INF | 0
j17 | t19 | 99 | 143.3969 | INF | 0
j17 | t20 | 99 | 143.3458 | INF | 0
j17 | t21 | 99 | 143.2929 | INF | 0
j17 | t22 | 99 | 143.3886 | INF | 0
j17 | t23 | 99 | 143.3619 | INF | 0
j17 | t24 | 99 | 143.3179 | INF | 0
j19 | t1 | 110 | 139.6265 | INF | 0
j19 | t2 | 110 | 139.5992 | INF | 0
j19 | t3 | 110 | 139.5898 | INF | 0
j19 | t4 | 110 | 139.5863 | INF | 0
j19 | t5 | 110 | 139.5819 | INF | 0
j19 | t6 | 110 | 139.81 | INF | 0
j19 | t7 | 110 | 140.3227 | INF | 0
j19 | t8 | 110 | 141.0706 | INF | 0
j19 | t9 | 110 | 141.9053 | INF | 0
j19 | t10 | 110 | 140.8646 | INF | 0
j19 | t11 | 110 | 141.1711 | INF | 0
j19 | t12 | 110 | 141.0054 | INF | 0
j19 | t13 | 110 | 140.8223 | INF | 0
j19 | t14 | 110 | 140.6829 | INF | 0
j19 | t15 | 110 | 140.5521 | INF | 0
j19 | t16 | 110 | 140.4388 | INF | 0
j19 | t17 | 110 | 140.3254 | INF | 0
j19 | t18 | 110 | 140.2688 | INF | 0
j19 | t19 | 110 | 140.1656 | INF | 0
j19 | t20 | 110 | 140.0959 | INF | 0
j19 | t21 | 110 | 140.0237 | INF | 0
j19 | t22 | 110 | 140.1542 | INF | 0
j19 | t23 | 110 | 140.1178 | INF | 0
j19 | t24 | 110 | 140.0578 | INF | 0
j21 | t1 | 102 | 136.1662 | INF | 0
j21 | t2 | 102 | 136.1314 | INF | 0
j21 | t3 | 102 | 136.1195 | INF | 0
j21 | t4 | 102 | 136.115 | INF | 0
j21 | t5 | 102 | 136.1095 | INF | 0
j21 | t6 | 102 | 136.3997 | INF | 0
j21 | t7 | 102 | 137.0522 | INF | 0
j21 | t8 | 102 | 137.9678 | INF | 0
j21 | t9 | 102 | 138.4581 | INF | 0
j21 | t10 | 102 | 138.0254 | INF | 0
j21 | t11 | 102 | 137.6313 | INF | 0
j21 | t12 | 102 | 137.4131 | INF | 0
j21 | t13 | 102 | 137.1718 | INF | 0
j21 | t14 | 102 | 136.9881 | INF | 0
j21 | t15 | 102 | 136.8158 | INF | 0
j21 | t16 | 102 | 136.6664 | INF | 0
j21 | t17 | 102 | 136.5171 | INF | 0
j21 | t18 | 102 | 136.4425 | INF | 0
j21 | t19 | 102 | 136.3066 | INF | 0
j21 | t20 | 102 | 136.2147 | INF | 0
j21 | t21 | 102 | 136.1196 | INF | 0
j21 | t22 | 102 | 136.2916 | INF | 0
j21 | t23 | 102 | 136.2436 | INF | 0
j21 | t24 | 102 | 136.1646 | INF | 0
j24 | t1 | 87 | 144.6014 | INF | 0
j24 | t2 | 87 | 144.5848 | INF | 0
j24 | t3 | 87 | 144.5791 | INF | 0
j24 | t4 | 87 | 144.5769 | INF | 0
j24 | t5 | 87 | 144.5743 | INF | 0
j24 | t6 | 87 | 144.713 | INF | 0
j24 | t7 | 87 | 145.0247 | INF | 0
j24 | t8 | 87 | 145.4795 | INF | 0
j24 | t9 | 87 | 144.6591 | INF | 0
j24 | t10 | 87 | 143.825 | INF | 0
j24 | t11 | 87 | 145.1827 | INF | 0
j24 | t12 | 87 | 145.0767 | INF | 0
j24 | t13 | 87 | 144.9594 | INF | 0
j24 | t14 | 87 | 144.8701 | INF | 0
j24 | t15 | 87 | 144.7864 | INF | 0
j24 | t16 | 87 | 144.7139 | INF | 0
j24 | t17 | 87 | 144.6413 | INF | 0
j24 | t18 | 87 | 144.605 | INF | 0
j24 | t19 | 87 | 144.539 | INF | 0
j24 | t20 | 87 | 144.4944 | INF | 0
j24 | t21 | 87 | 144.4482 | INF | 0
j24 | t22 | 87 | 144.5317 | INF | 0
j24 | t23 | 87 | 144.5084 | INF | 0
j24 | t24 | 87 | 144.47 | INF | 0
j26 | t1 | 87 | 138.3988 | INF | 0
j26 | t2 | 87 | 138.2711 | INF | 0
j26 | t3 | 87 | 138.2608 | INF | 0
j26 | t4 | 87 | 138.2569 | INF | 0
j26 | t5 | 87 | 139.7663 | INF | 0
j26 | t6 | 87 | 139.5082 | INF | 0
j26 | t7 | 87 | 139.0664 | INF | 0
j26 | t8 | 87 | 140.7029 | INF | 0
j26 | t9 | 87 | 144.385 | INF | 0
j26 | t10 | 87 | 140.8447 | INF | 0
j26 | t11 | 87 | 137.8661 | INF | 0
j26 | t12 | 87 | 137.6517 | INF | 0
j26 | t13 | 87 | 137.4146 | INF | 0
j26 | t14 | 87 | 137.234 | INF | 0
j26 | t15 | 87 | 138.2114 | INF | 0
j26 | t16 | 87 | 136.9179 | INF | 0
j26 | t17 | 87 | 136.7712 | INF | 0
j26 | t18 | 87 | 136.6978 | INF | 0
j26 | t19 | 87 | 136.5643 | INF | 0
j26 | t20 | 87 | 136.474 | INF | 0
j26 | t21 | 87 | 136.3806 | INF | 0
j26 | t22 | 87 | 136.5495 | INF | 0
j26 | t23 | 87 | 136.5024 | INF | 0
j26 | t24 | 87 | 136.6902 | INF | 0
j27 | t1 | 88 | 138.024 | INF | 0
j27 | t2 | 88 | 136.916 | INF | 0
j27 | t3 | 88 | 136.178 | INF | 0
j27 | t4 | 88 | 138.2569 | INF | 0
j27 | t5 | 88 | 139.7489 | INF | 0
j27 | t6 | 88 | 139.5082 | INF | 0
j27 | t7 | 88 | 136.8167 | INF | 0
j27 | t8 | 88 | 140.6435 | INF | 0
j27 | t9 | 88 | 144.3774 | INF | 0
j27 | t10 | 88 | 140.5633 | INF | 0
j27 | t11 | 88 | 137.3689 | INF | 0
j27 | t12 | 88 | 137.6517 | INF | 0
j27 | t13 | 88 | 134.5659 | INF | 0
j27 | t14 | 88 | 136.1473 | INF | 0
j27 | t15 | 88 | 137.8949 | INF | 0
j27 | t16 | 88 | 136.9145 | INF | 0
j27 | t17 | 88 | 133.7996 | INF | 0
j27 | t18 | 88 | 136.6605 | INF | 0
j27 | t19 | 88 | 136.5643 | INF | 0
j27 | t20 | 88 | 133.4457 | INF | 0
j27 | t21 | 88 | 136.3492 | INF | 0
j27 | t22 | 88 | 134.7531 | INF | 0
j27 | t23 | 88 | 135.9555 | INF | 0
j27 | t24 | 88 | 136.0637 | INF | 0
j30 | t1 | 48 | 135.6486 | INF | 0
j30 | t2 | 48 | 137.7541 | INF | 0
j30 | t3 | 48 | 138.2087 | INF | 0
j30 | t4 | 48 | 130.9974 | INF | 0
j30 | t5 | 48 | 135.0498 | INF | 0
j30 | t6 | 48 | 133.5297 | INF | 0
j30 | t7 | 48 | 139.0664 | INF | 0
j30 | t8 | 48 | 136.813 | INF | 0
j30 | t9 | 48 | 144.176 | INF | 0
j30 | t10 | 48 | 139.882 | INF | 0
j30 | t11 | 48 | 134.8863 | INF | 0
j30 | t12 | 48 | 129.1229 | INF | 0
j30 | t13 | 48 | 137.4146 | INF | 0
j30 | t14 | 48 | 135.7927 | INF | 0
j30 | t15 | 48 | 134.8852 | INF | 0
j30 | t16 | 48 | 128.3085 | INF | 0
j30 | t17 | 48 | 136.7712 | INF | 0
j30 | t18 | 48 | 129.2405 | INF | 0
j30 | t19 | 48 | 127.4041 | INF | 0
j30 | t20 | 48 | 136.474 | INF | 0
j30 | t21 | 48 | 128.6044 | INF | 0
j30 | t22 | 48 | 135.992 | INF | 0
j30 | t23 | 48 | 133.2628 | INF | 0
j30 | t24 | 48 | 133.9141 | INF | 0
j2 | t1 | 74 | 145.1123 | INF | 0
j2 | t2 | 74 | 145.0969 | INF | 0
j2 | t3 | 74 | 145.0916 | INF | 0
j2 | t4 | 74 | 145.0896 | INF | 0
j2 | t5 | 74 | 145.0871 | INF | 0
j2 | t6 | 74 | 145.216 | INF | 0
j2 | t7 | 74 | 145.5057 | INF | 0
j2 | t8 | 74 | 145.9284 | INF | 0
j2 | t9 | 74 | 144.9644 | INF | 0
j2 | t10 | 74 | 145.2741 | INF | 0
j2 | t11 | 74 | 148.1619 | INF | 0
j2 | t12 | 74 | 148.1004 | INF | 0
j2 | t13 | 74 | 148.0324 | INF | 0
j2 | t14 | 74 | 147.9807 | INF | 0
j2 | t15 | 74 | 147.9321 | INF | 0
j2 | t16 | 74 | 147.89 | INF | 0
j2 | t17 | 74 | 147.848 | INF | 0
j2 | t18 | 74 | 147.8269 | INF | 0
j2 | t19 | 74 | 147.7887 | INF | 0
j2 | t20 | 74 | 147.7628 | INF | 0
j2 | t21 | 74 | 147.736 | INF | 0
j2 | t22 | 74 | 147.7844 | INF | 0
j2 | t23 | 74 | 147.7709 | INF | 0
j2 | t24 | 74 | 147.7487 | INF | 0
j3 | t1 | 75 | 142.713 | INF | 0
j3 | t2 | 75 | 140.7882 | INF | 0
j3 | t3 | 75 | 116.4278 | INF | 0
j3 | t4 | 75 | 139.6545 | INF | 0
j3 | t5 | 75 | 145.0871 | INF | 0
j3 | t6 | 75 | 145.2159 | INF | 0
j3 | t7 | 75 | 141.2715 | INF | 0
j3 | t8 | 75 | 140.9402 | INF | 0
j3 | t9 | 75 | 144.84 | INF | 0
j3 | t10 | 75 | 144.5091 | INF | 0
j3 | t11 | 75 | 146.9953 | INF | 0
j3 | t12 | 75 | 138.7439 | INF | 0
j3 | t13 | 75 | 148.0324 | INF | 0
j3 | t14 | 75 | 144.4882 | INF | 0
j3 | t15 | 75 | 147.9321 | INF | 0
j3 | t16 | 75 | 147.89 | INF | 0
j3 | t17 | 75 | 128.4457 | INF | 0
j3 | t18 | 75 | 147.8269 | INF | 0
j3 | t19 | 75 | 147.7281 | INF | 0
j3 | t20 | 75 | 147.7628 | INF | 0
j3 | t21 | 75 | 144.281 | INF | 0
j3 | t22 | 75 | 147.7844 | INF | 0
j3 | t23 | 75 | 147.7709 | INF | 0
j3 | t24 | 75 | 145.3265 | INF | 0
j6 | t1 | 56 | 135.1706 | INF | 0
j6 | t2 | 56 | 136.339 | INF | 0
j6 | t3 | 56 | 142.0967 | INF | 0
j6 | t4 | 56 | 136.8794 | INF | 0
j6 | t5 | 56 | 131.176 | INF | 0
j6 | t6 | 56 | 131.5577 | INF | 0
j6 | t7 | 56 | 137.3284 | INF | 0
j6 | t8 | 56 | 138.7455 | INF | 0
j6 | t9 | 56 | 143.612 | INF | 0
j6 | t10 | 56 | 143.1774 | INF | 0
j6 | t11 | 56 | 144.9939 | INF | 0
j6 | t12 | 56 | 146.9914 | INF | 0
j6 | t13 | 56 | 143.1592 | INF | 0
j6 | t14 | 56 | 145.6388 | INF | 0
j6 | t15 | 56 | 142.9461 | INF | 0
j6 | t16 | 56 | 142.8567 | INF | 0
j6 | t17 | 56 | 147.4742 | INF | 0
j6 | t18 | 56 | 142.7227 | INF | 0
j6 | t19 | 56 | 143.0064 | INF | 0
j6 | t20 | 56 | 142.5864 | INF | 0
j6 | t21 | 56 | 145.1914 | INF | 0
j6 | t22 | 56 | 142.6324 | INF | 0
j6 | t23 | 56 | 142.6037 | INF | 0
j6 | t24 | 56 | 144.8397 | INF | 0
j7 | t1 | 64 | 132.4627 | INF | 0
j7 | t2 | 64 | 135.6412 | INF | 0
j7 | t3 | 64 | 137.3937 | INF | 0
j7 | t4 | 64 | 136.3345 | INF | 0
j7 | t5 | 64 | 127.3592 | INF | 0
j7 | t6 | 64 | 128.6641 | INF | 0
j7 | t7 | 64 | 125.2399 | INF | 0
j7 | t8 | 64 | 133.8051 | INF | 0
j7 | t9 | 64 | 142.4938 | INF | 0
j7 | t10 | 64 | 141.5152 | INF | 0
j7 | t11 | 64 | 140.0191 | INF | 0
j7 | t12 | 64 | 145.25 | INF | 0
j7 | t13 | 64 | 138.7398 | INF | 0
j7 | t14 | 64 | 145.1451 | INF | 0
j7 | t15 | 64 | 137.6674 | INF | 0
j7 | t16 | 64 | 142.8567 | INF | 0
j7 | t17 | 64 | 146.9437 | INF | 0
j7 | t18 | 64 | 142.7227 | INF | 0
j7 | t19 | 64 | 140.9036 | INF | 0
j7 | t20 | 64 | 139.6154 | INF | 0
j7 | t21 | 64 | 144.7023 | INF | 0
j7 | t22 | 64 | 139.9314 | INF | 0
j7 | t23 | 64 | 141.6646 | INF | 0
j7 | t24 | 64 | 142.2011 | INF | 0
j10 | t1 | 73 | 121.1486 | INF | 0
j10 | t2 | 73 | 114.7199 | INF | 0
j10 | t3 | 73 | 142.0967 | INF | 0
j10 | t4 | 73 | 115.569 | INF | 0
j10 | t5 | 73 | 111.757 | INF | 0
j10 | t6 | 73 | 109.0738 | INF | 0
j10 | t7 | 73 | 137.2773 | INF | 0
j10 | t8 | 73 | 135.2228 | INF | 0
j10 | t9 | 73 | 143.1221 | INF | 0
j10 | t10 | 73 | 142.366 | INF | 0
j10 | t11 | 73 | 144.9939 | INF | 0
j10 | t12 | 73 | 146.9914 | INF | 0
j10 | t13 | 73 | 141.8979 | INF | 0
j10 | t14 | 73 | 141.6308 | INF | 0
j10 | t15 | 73 | 142.2037 | INF | 0
j10 | t16 | 73 | 122.8583 | INF | 0
j10 | t17 | 73 | 147.4628 | INF | 0
j10 | t18 | 73 | 122.4414 | INF | 0
j10 | t19 | 73 | 138.4979 | INF | 0
j10 | t20 | 73 | 139.1143 | INF | 0
j10 | t21 | 73 | 140.6248 | INF | 0
j10 | t22 | 73 | 138.7095 | INF | 0
j10 | t23 | 73 | 133.2182 | INF | 0
j10 | t24 | 73 | 144.0631 | INF | 0

## Charge_r
TOC
Charge_r | (equation) | Niveau de charge au rÃ©servoir (r) Ã (t)
n | t | Lowerbound | Value | Upperbound | Marginal
r12 | t1 | 91 | 141.117 | INF | 0
r12 | t2 | 91 | 140.8289 | INF | 0
r12 | t3 | 91 | 140.4765 | INF | 0
r12 | t4 | 91 | 140.1747 | INF | 0
r12 | t5 | 91 | 139.8723 | INF | 0
r12 | t6 | 91 | 139.6525 | INF | 0
r12 | t7 | 91 | 139.5716 | INF | 0
r12 | t8 | 91 | 139.7074 | INF | 0
r12 | t9 | 91 | 139.3983 | INF | 0
r12 | t10 | 91 | 138.6033 | INF | 0
r12 | t11 | 91 | 140.5139 | INF | 0
r12 | t12 | 91 | 140.5741 | INF | 0
r12 | t13 | 91 | 140.7345 | INF | 0
r12 | t14 | 91 | 140.9081 | INF | 0
r12 | t15 | 91 | 141.0706 | INF | 0
r12 | t16 | 91 | 141.1802 | INF | 0
r12 | t17 | 91 | 141.2271 | INF | 0
r12 | t18 | 91 | 141.3427 | INF | 0
r12 | t19 | 91 | 141.3133 | INF | 0
r12 | t20 | 91 | 141.311 | INF | 0
r12 | t21 | 91 | 141.4802 | INF | 0
r12 | t22 | 91 | 141.8962 | INF | 0
r12 | t23 | 91 | 142.157 | INF | 0
r12 | t24 | 91 | 142.3476 | INF | 0
r13 | t1 | 116 | 135.8583 | INF | 0
r13 | t2 | 116 | 135.6402 | INF | 0
r13 | t3 | 116 | 135.4336 | INF | 0
r13 | t4 | 116 | 135.2454 | INF | 0
r13 | t5 | 116 | 135.0675 | INF | 0
r13 | t6 | 116 | 135.1857 | INF | 0
r13 | t7 | 116 | 135.6402 | INF | 0
r13 | t8 | 116 | 136.3985 | INF | 0
r13 | t9 | 116 | 141.1419 | INF | 0
r13 | t10 | 116 | 140.3784 | INF | 0
r13 | t11 | 116 | 141.5366 | INF | 0
r13 | t12 | 116 | 141.5176 | INF | 0
r13 | t13 | 116 | 141.5199 | INF | 0
r13 | t14 | 116 | 141.5201 | INF | 0
r13 | t15 | 116 | 141.5267 | INF | 0
r13 | t16 | 116 | 141.546 | INF | 0
r13 | t17 | 116 | 141.5312 | INF | 0
r13 | t18 | 116 | 141.5921 | INF | 0
r13 | t19 | 116 | 141.5848 | INF | 0
r13 | t20 | 116 | 141.602 | INF | 0
r13 | t21 | 116 | 141.6857 | INF | 0
r13 | t22 | 116 | 141.8838 | INF | 0
r13 | t23 | 116 | 141.9595 | INF | 0
r13 | t24 | 116 | 142.018 | INF | 0
r132 | t1 | 100 | 135.5416 | INF | 0
r132 | t2 | 100 | 135.3234 | INF | 0
r132 | t3 | 100 | 135.0896 | INF | 0
r132 | t4 | 100 | 134.7431 | INF | 0
r132 | t5 | 100 | 134.413 | INF | 0
r132 | t6 | 100 | 134.343 | INF | 0
r132 | t7 | 100 | 134.5353 | INF | 0
r132 | t8 | 100 | 135.093 | INF | 0
r132 | t9 | 100 | 136.6353 | INF | 0
r132 | t10 | 100 | 135.402 | INF | 0
r132 | t11 | 100 | 135.6545 | INF | 0
r132 | t12 | 100 | 135.7096 | INF | 0
r132 | t13 | 100 | 135.8348 | INF | 0
r132 | t14 | 100 | 135.8672 | INF | 0
r132 | t15 | 100 | 135.8702 | INF | 0
r132 | t16 | 100 | 135.9048 | INF | 0
r132 | t17 | 100 | 135.9271 | INF | 0
r132 | t18 | 100 | 136.0246 | INF | 0
r132 | t19 | 100 | 135.9883 | INF | 0
r132 | t20 | 100 | 136.0074 | INF | 0
r132 | t21 | 100 | 136.0143 | INF | 0
r132 | t22 | 100 | 136.3151 | INF | 0
r132 | t23 | 100 | 136.5138 | INF | 0
r132 | t24 | 100 | 136.5921 | INF | 0
r133 | t1 | 81 | 130.7874 | INF | 0
r133 | t2 | 81 | 130.476 | INF | 0
r133 | t3 | 81 | 129.7792 | INF | 0
r133 | t4 | 81 | 128.9757 | INF | 0
r133 | t5 | 81 | 128.0643 | INF | 0
r133 | t6 | 81 | 128.0878 | INF | 0
r133 | t7 | 81 | 128.7234 | INF | 0
r133 | t8 | 81 | 129.8077 | INF | 0
r133 | t9 | 81 | 130.2579 | INF | 0
r133 | t10 | 81 | 129.6363 | INF | 0
r133 | t11 | 81 | 128.7025 | INF | 0
r133 | t12 | 81 | 129.1466 | INF | 0
r133 | t13 | 81 | 129.9031 | INF | 0
r133 | t14 | 81 | 130.4195 | INF | 0
r133 | t15 | 81 | 130.5649 | INF | 0
r133 | t16 | 81 | 130.3209 | INF | 0
r133 | t17 | 81 | 129.9743 | INF | 0
r133 | t18 | 81 | 129.6084 | INF | 0
r133 | t19 | 81 | 128.961 | INF | 0
r133 | t20 | 81 | 128.3178 | INF | 0
r133 | t21 | 81 | 128.4016 | INF | 0
r133 | t22 | 81 | 130.0483 | INF | 0
r133 | t23 | 81 | 130.9181 | INF | 0
r133 | t24 | 81 | 130.85 | INF | 0
r134 | t1 | 131 | 131 | INF | 0.021677
r134 | t2 | 131 | 131 | INF | 0.021654
r134 | t3 | 131 | 131 | INF | 0.021646
r134 | t4 | 131 | 131 | INF | 0.021643
r134 | t5 | 131 | 131 | INF | 0.021639
r134 | t6 | 131 | 131 | INF | 0.021835
r134 | t7 | 131 | 131 | INF | 0.022297
r134 | t8 | 131 | 131 | INF | 0.023025
r134 | t9 | 131 | 131 | INF | 0.0070735
r134 | t10 | 131 | 131 | INF | 0.0079048
r134 | t11 | 131 | 131 | INF | 0.016573
r134 | t12 | 131 | 131 | INF | 0.016452
r134 | t13 | 131 | 131 | INF | 0.01632
r134 | t14 | 131 | 131 | INF | 0.016222
r134 | t15 | 131 | 131 | INF | 0.016132
r134 | t16 | 131 | 131 | INF | 0.016055
r134 | t17 | 131 | 131 | INF | 0.015979
r134 | t18 | 131 | 131 | INF | 0.015941
r134 | t19 | 131 | 131 | INF | 0.015874
r134 | t20 | 131 | 131 | INF | 0.015828
r134 | t21 | 131 | 131 | INF | 0.015782
r134 | t22 | 131 | 131 | INF | 0.015866
r134 | t23 | 131 | 131 | INF | 0.015842
r134 | t24 | 131 | 131 | INF | 0.015804
r14 | t1 | 97 | 142.7998 | INF | 0
r14 | t2 | 97 | 142.7848 | INF | 0
r14 | t3 | 97 | 142.7791 | INF | 0
r14 | t4 | 97 | 142.7769 | INF | 0
r14 | t5 | 97 | 141.9787 | INF | 0
r14 | t6 | 97 | 141.9207 | INF | 0
r14 | t7 | 97 | 142.3491 | INF | 0
r14 | t8 | 97 | 142.4245 | INF | 0
r14 | t9 | 97 | 141.6891 | INF | 0
r14 | t10 | 97 | 140.8433 | INF | 0
r14 | t11 | 97 | 142.6241 | INF | 0
r14 | t12 | 97 | 142.8781 | INF | 0
r14 | t13 | 97 | 142.7866 | INF | 0
r14 | t14 | 97 | 142.8323 | INF | 0
r14 | t15 | 97 | 142.3581 | INF | 0
r14 | t16 | 97 | 142.5351 | INF | 0
r14 | t17 | 97 | 142.4625 | INF | 0
r14 | t18 | 97 | 142.4777 | INF | 0
r14 | t19 | 97 | 142.4888 | INF | 0
r14 | t20 | 97 | 142.4441 | INF | 0
r14 | t21 | 97 | 142.5137 | INF | 0
r14 | t22 | 97 | 142.7065 | INF | 0
r14 | t23 | 97 | 142.6832 | INF | 0
r14 | t24 | 97 | 142.663 | INF | 0
r15 | t1 | 61 | 133.2299 | INF | 0
r15 | t2 | 61 | 134.9217 | INF | 0
r15 | t3 | 61 | 135.9502 | INF | 0
r15 | t4 | 61 | 128.7974 | INF | 0
r15 | t5 | 61 | 123.1362 | INF | 0
r15 | t6 | 61 | 129.9484 | INF | 0
r15 | t7 | 61 | 135.5595 | INF | 0
r15 | t8 | 61 | 132.9708 | INF | 0
r15 | t9 | 61 | 140.5163 | INF | 0
r15 | t10 | 61 | 136.1418 | INF | 0
r15 | t11 | 61 | 131.6063 | INF | 0
r15 | t12 | 61 | 125.1132 | INF | 0
r15 | t13 | 61 | 134.8184 | INF | 0
r15 | t14 | 61 | 131.146 | INF | 0
r15 | t15 | 61 | 130.8165 | INF | 0
r15 | t16 | 61 | 125.7419 | INF | 0
r15 | t17 | 61 | 134.5712 | INF | 0
r15 | t18 | 61 | 123.6715 | INF | 0
r15 | t19 | 61 | 124.935 | INF | 0
r15 | t20 | 61 | 134.274 | INF | 0
r15 | t21 | 61 | 118.7415 | INF | 0
r15 | t22 | 61 | 133.3671 | INF | 0
r15 | t23 | 61 | 131.0612 | INF | 0
r15 | t24 | 61 | 131.3808 | INF | 0
r151 | t1 | 91 | 127.4288 | INF | 0
r151 | t2 | 91 | 133.5323 | INF | 0
r151 | t3 | 91 | 134.0109 | INF | 0
r151 | t4 | 91 | 109.7708 | INF | 0
r151 | t5 | 91 | 130.2673 | INF | 0
r151 | t6 | 91 | 114.6383 | INF | 0
r151 | t7 | 91 | 133.6694 | INF | 0
r151 | t8 | 91 | 124.8983 | INF | 0
r151 | t9 | 91 | 138.1475 | INF | 0
r151 | t10 | 91 | 132.8547 | INF | 0
r151 | t11 | 91 | 122.922 | INF | 0
r151 | t12 | 91 | 111.7678 | INF | 0
r151 | t13 | 91 | 132.3452 | INF | 0
r151 | t14 | 91 | 131.1427 | INF | 0
r151 | t15 | 91 | 128.0439 | INF | 0
r151 | t16 | 91 | 103.95 | INF | 0
r151 | t17 | 91 | 132.2479 | INF | 0
r151 | t18 | 91 | 119.5349 | INF | 0
r151 | t19 | 91 | 101.4281 | INF | 0
r151 | t20 | 91 | 131.5701 | INF | 0
r151 | t21 | 91 | 122.2899 | INF | 0
r151 | t22 | 91 | 130.694 | INF | 0
r151 | t23 | 91 | 121.9143 | INF | 0
r151 | t24 | 91 | 126.2727 | INF | 0
r16 | t1 | 106 | 135.2226 | INF | 0
r16 | t2 | 106 | 134.1148 | INF | 0
r16 | t3 | 106 | 133.2512 | INF | 0
r16 | t4 | 106 | 135.4569 | INF | 0
r16 | t5 | 106 | 136.7467 | INF | 0
r16 | t6 | 106 | 136.5319 | INF | 0
r16 | t7 | 106 | 132.7896 | INF | 0
r16 | t8 | 106 | 136.6284 | INF | 0
r16 | t9 | 106 | 140.3623 | INF | 0
r16 | t10 | 106 | 136.5475 | INF | 0
r16 | t11 | 106 | 133.3529 | INF | 0
r16 | t12 | 106 | 133.9367 | INF | 0
r16 | t13 | 106 | 130.7006 | INF | 0
r16 | t14 | 106 | 132.618 | INF | 0
r16 | t15 | 106 | 134.7199 | INF | 0
r16 | t16 | 106 | 134.1145 | INF | 0
r16 | t17 | 106 | 130.7893 | INF | 0
r16 | t18 | 106 | 133.5291 | INF | 0
r16 | t19 | 106 | 133.7643 | INF | 0
r16 | t20 | 106 | 129.9563 | INF | 0
r16 | t21 | 106 | 133.1992 | INF | 0
r16 | t22 | 106 | 131.9531 | INF | 0
r16 | t23 | 106 | 133.1305 | INF | 0
r16 | t24 | 106 | 133.2623 | INF | 0
r161 | t1 | 93 | 130.156 | INF | 0
r161 | t2 | 93 | 115.39 | INF | 0
r161 | t3 | 93 | 104.8475 | INF | 0
r161 | t4 | 93 | 132.8209 | INF | 0
r161 | t5 | 93 | 134.5507 | INF | 0
r161 | t6 | 93 | 134.5774 | INF | 0
r161 | t7 | 93 | 113.3457 | INF | 0
r161 | t8 | 93 | 134.1257 | INF | 0
r161 | t9 | 93 | 138.5027 | INF | 0
r161 | t10 | 93 | 131.8917 | INF | 0
r161 | t11 | 93 | 126.0531 | INF | 0
r161 | t12 | 93 | 132.4447 | INF | 0
r161 | t13 | 93 | 94.5364 | INF | 0
r161 | t14 | 93 | 113.9153 | INF | 0
r161 | t15 | 93 | 127.776 | INF | 0
r161 | t16 | 93 | 132.0506 | INF | 0
r161 | t17 | 93 | 93 | INF | 0
r161 | t18 | 93 | 131.7067 | INF | 0
r161 | t19 | 93 | 132.1643 | INF | 0
r161 | t20 | 93 | 100.172 | INF | 0
r161 | t21 | 93 | 131.5325 | INF | 0
r161 | t22 | 93 | 102.6981 | INF | 0
r161 | t23 | 93 | 126.1241 | INF | 0
r161 | t24 | 93 | 125.046 | INF | 0
r17 | t1 | 92 | 138.9025 | INF | 0
r17 | t2 | 92 | 137.4851 | INF | 0
r17 | t3 | 92 | 110.0483 | INF | 0
r17 | t4 | 92 | 134.1474 | INF | 0
r17 | t5 | 92 | 139.7735 | INF | 0
r17 | t6 | 92 | 140.1306 | INF | 0
r17 | t7 | 92 | 136.3794 | INF | 0
r17 | t8 | 92 | 135.3282 | INF | 0
r17 | t9 | 92 | 139.338 | INF | 0
r17 | t10 | 92 | 138.9972 | INF | 0
r17 | t11 | 92 | 141.4233 | INF | 0
r17 | t12 | 92 | 133.1608 | INF | 0
r17 | t13 | 92 | 143.4004 | INF | 0
r17 | t14 | 92 | 139.7746 | INF | 0
r17 | t15 | 92 | 144.0195 | INF | 0
r17 | t16 | 92 | 144.59 | INF | 0
r17 | t17 | 92 | 121.7757 | INF | 0
r17 | t18 | 92 | 142.8017 | INF | 0
r17 | t19 | 92 | 143.0803 | INF | 0
r17 | t20 | 92 | 143.6221 | INF | 0
r17 | t21 | 92 | 139.3435 | INF | 0
r17 | t22 | 92 | 143.7953 | INF | 0
r17 | t23 | 92 | 144.4709 | INF | 0
r17 | t24 | 92 | 141.9689 | INF | 0
r171 | t1 | 80 | 138.9129 | INF | 0
r171 | t2 | 80 | 80 | INF | 0
r171 | t3 | 80 | 80.0613 | INF | 0
r171 | t4 | 80 | 80 | INF | 0
r171 | t5 | 80 | 140.2917 | INF | 0
r171 | t6 | 80 | 140.5405 | INF | 0
r171 | t7 | 80 | 80 | INF | 0
r171 | t8 | 80 | 124.0841 | INF | 0
r171 | t9 | 80 | 138.4111 | INF | 0
r171 | t10 | 80 | 135.7177 | INF | 0
r171 | t11 | 80 | 141.591 | INF | 0
r171 | t12 | 80 | 83.6103 | INF | 0
r171 | t13 | 80 | 142.6391 | INF | 0
r171 | t14 | 80 | 133.6827 | INF | 0
r171 | t15 | 80 | 143.0083 | INF | 0
r171 | t16 | 80 | 143.1846 | INF | 0
r171 | t17 | 80 | 124.0004 | INF | 0
r171 | t18 | 80 | 143.7201 | INF | 0
r171 | t19 | 80 | 143.6571 | INF | 0
r171 | t20 | 80 | 144.0567 | INF | 0
r171 | t21 | 80 | 140.866 | INF | 0
r171 | t22 | 80 | 144.7497 | INF | 0
r171 | t23 | 80 | 144.9709 | INF | 0
r171 | t24 | 80 | 137.4167 | INF | 0
r18 | t1 | 86 | 116.0817 | INF | 0
r18 | t2 | 86 | 110.9695 | INF | 0
r18 | t3 | 86 | 138.7431 | INF | 0
r18 | t4 | 86 | 112.269 | INF | 0
r18 | t5 | 86 | 86 | INF | 0
r18 | t6 | 86 | 86 | INF | 0
r18 | t7 | 86 | 131.3885 | INF | 0
r18 | t8 | 86 | 129.1066 | INF | 0
r18 | t9 | 86 | 136.8395 | INF | 0
r18 | t10 | 86 | 134.4093 | INF | 0
r18 | t11 | 86 | 139.8471 | INF | 0
r18 | t12 | 86 | 142.3972 | INF | 0
r18 | t13 | 86 | 137.7848 | INF | 0
r18 | t14 | 86 | 133.8089 | INF | 0
r18 | t15 | 86 | 128.8858 | INF | 0
r18 | t16 | 86 | 118.6613 | INF | 0
r18 | t17 | 86 | 143.5657 | INF | 0
r18 | t18 | 86 | 118.8383 | INF | 0
r18 | t19 | 86 | 135.1978 | INF | 0
r18 | t20 | 86 | 91.3505 | INF | 0
r18 | t21 | 86 | 136.3386 | INF | 0
r18 | t22 | 86 | 134.8035 | INF | 0
r18 | t23 | 86 | 129.6508 | INF | 0
r18 | t24 | 86 | 140.763 | INF | 0
r181 | t1 | 91 | 105.7543 | INF | 0
r181 | t2 | 91 | 91 | INF | 0
r181 | t3 | 91 | 137.3046 | INF | 0
r181 | t4 | 91 | 91 | INF | 0
r181 | t5 | 91 | 97.0619 | INF | 0
r181 | t6 | 91 | 91 | INF | 0
r181 | t7 | 91 | 130.9798 | INF | 0
r181 | t8 | 91 | 126.0632 | INF | 0
r181 | t9 | 91 | 136.316 | INF | 0
r181 | t10 | 91 | 135.5572 | INF | 0
r181 | t11 | 91 | 138.498 | INF | 0
r181 | t12 | 91 | 140.5849 | INF | 0
r181 | t13 | 91 | 134.1909 | INF | 0
r181 | t14 | 91 | 133.0611 | INF | 0
r181 | t15 | 91 | 136.2835 | INF | 0
r181 | t16 | 91 | 98.9068 | INF | 0
r181 | t17 | 91 | 142.385 | INF | 0
r181 | t18 | 91 | 98.8195 | INF | 0
r181 | t19 | 91 | 129.1245 | INF | 0
r181 | t20 | 91 | 134.3867 | INF | 0
r181 | t21 | 91 | 131.8671 | INF | 0
r181 | t22 | 91 | 130.5275 | INF | 0
r181 | t23 | 91 | 119.8152 | INF | 0
r181 | t24 | 91 | 138.6863 | INF | 0
r19 | t1 | 75 | 120.3044 | INF | 0
r19 | t2 | 75 | 121.8531 | INF | 0
r19 | t3 | 75 | 75.1144 | INF | 0
r19 | t4 | 75 | 123.6222 | INF | 0
r19 | t5 | 75 | 75 | INF | 0
r19 | t6 | 75 | 121.6265 | INF | 0
r19 | t7 | 75 | 118.3165 | INF | 0
r19 | t8 | 75 | 108.8413 | INF | 0
r19 | t9 | 75 | 131.9445 | INF | 0
r19 | t10 | 75 | 132.7005 | INF | 0
r19 | t11 | 75 | 119.1109 | INF | 0
r19 | t12 | 75 | 122.4362 | INF | 0
r19 | t13 | 75 | 116.1942 | INF | 0
r19 | t14 | 75 | 132.506 | INF | 0
r19 | t15 | 75 | 130.9777 | INF | 0
r19 | t16 | 75 | 136.5218 | INF | 0
r19 | t17 | 75 | 134.6605 | INF | 0
r19 | t18 | 75 | 136.7586 | INF | 0
r19 | t19 | 75 | 110.0434 | INF | 0
r19 | t20 | 75 | 133.7048 | INF | 0
r19 | t21 | 75 | 133.4035 | INF | 0
r19 | t22 | 75 | 109.1148 | INF | 0
r19 | t23 | 75 | 128.9185 | INF | 0
r19 | t24 | 75 | 124.9921 | INF | 0
r191 | t1 | 87 | 126.8369 | INF | 0
r191 | t2 | 87 | 131.3301 | INF | 0
r191 | t3 | 87 | 133.1751 | INF | 0
r191 | t4 | 87 | 132.1805 | INF | 0
r191 | t5 | 87 | 123.2591 | INF | 0
r191 | t6 | 87 | 119.8924 | INF | 0
r191 | t7 | 87 | 102.0278 | INF | 0
r191 | t8 | 87 | 126.4057 | INF | 0
r191 | t9 | 87 | 136.2101 | INF | 0
r191 | t10 | 87 | 134.3636 | INF | 0
r191 | t11 | 87 | 132.2003 | INF | 0
r191 | t12 | 87 | 139.7578 | INF | 0
r191 | t13 | 87 | 131.8614 | INF | 0
r191 | t14 | 87 | 140.0227 | INF | 0
r191 | t15 | 87 | 124.3909 | INF | 0
r191 | t16 | 87 | 137.6004 | INF | 0
r191 | t17 | 87 | 141.9425 | INF | 0
r191 | t18 | 87 | 137.7825 | INF | 0
r191 | t19 | 87 | 136.0991 | INF | 0
r191 | t20 | 87 | 130.3671 | INF | 0
r191 | t21 | 87 | 140.158 | INF | 0
r191 | t22 | 87 | 135.5847 | INF | 0
r191 | t23 | 87 | 137.4866 | INF | 0
r191 | t24 | 87 | 137.4333 | INF | 0

## Charge_s
TOC
Charge_s | (equation) | Niveau de charge Ã la source Ã (t)
n | c | d | t | Lowerbound | Value | Upperbound | Marginal
s | small | p1 | t1 | -INF | 70 | 70 | -0.010839
s | small | p1 | t2 | -INF | 70 | 70 | -0.010827
s | small | p1 | t3 | -INF | 70 | 70 | -0.010823
s | small | p1 | t4 | -INF | 70 | 70 | -0.010821
s | small | p1 | t5 | -INF | 70 | 70 | -0.01082
s | small | p1 | t6 | -INF | 70 | 70 | -0.010918
s | small | p1 | t7 | -INF | 70 | 70 | -0.011148
s | small | p1 | t8 | -INF | 70 | 70 | -0.011513
s | small | p1 | t9 | -INF | 70 | 70 | -0.0035367
s | small | p1 | t10 | -INF | 70 | 70 | -0.0039524
s | small | p1 | t11 | -INF | 70 | 70 | -0.0082866
s | small | p1 | t12 | -INF | 70 | 70 | -0.0082258
s | small | p1 | t13 | -INF | 70 | 70 | -0.0081601
s | small | p1 | t14 | -INF | 70 | 70 | -0.0081111
s | small | p1 | t15 | -INF | 70 | 70 | -0.0080659
s | small | p1 | t16 | -INF | 70 | 70 | -0.0080274
s | small | p1 | t17 | -INF | 70 | 70 | -0.0079894
s | small | p1 | t18 | -INF | 70 | 70 | -0.0079706
s | small | p1 | t19 | -INF | 70 | 70 | -0.0079368
s | small | p1 | t20 | -INF | 70 | 70 | -0.0079141
s | small | p1 | t21 | -INF | 70 | 70 | -0.0078909
s | small | p1 | t22 | -INF | 70 | 70 | -0.0079331
s | small | p1 | t23 | -INF | 70 | 70 | -0.0079212
s | small | p1 | t24 | -INF | 70 | 70 | -0.0079019
s | small | p2 | t1 | -INF | 70 | 70 | -0.010839
s | small | p2 | t2 | -INF | 70 | 70 | -0.010827
s | small | p2 | t3 | -INF | 70 | 70 | -0.010823
s | small | p2 | t4 | -INF | 70 | 70 | -0.010821
s | small | p2 | t5 | -INF | 70 | 70 | -0.01082
s | small | p2 | t6 | -INF | 70 | 70 | -0.010918
s | small | p2 | t7 | -INF | 70 | 70 | -0.011148
s | small | p2 | t8 | -INF | 70 | 70 | -0.011513
s | small | p2 | t9 | -INF | 70 | 70 | -0.0035367
s | small | p2 | t10 | -INF | 70 | 70 | -0.0039524
s | small | p2 | t11 | -INF | 70 | 70 | -0.0082866
s | small | p2 | t12 | -INF | 70 | 70 | -0.0082258
s | small | p2 | t13 | -INF | 70 | 70 | -0.0081601
s | small | p2 | t14 | -INF | 70 | 70 | -0.0081111
s | small | p2 | t15 | -INF | 70 | 70 | -0.0080659
s | small | p2 | t16 | -INF | 70 | 70 | -0.0080274
s | small | p2 | t17 | -INF | 70 | 70 | -0.0079894
s | small | p2 | t18 | -INF | 70 | 70 | -0.0079706
s | small | p2 | t19 | -INF | 70 | 70 | -0.0079368
s | small | p2 | t20 | -INF | 70 | 70 | -0.0079141
s | small | p2 | t21 | -INF | 70 | 70 | -0.0078909
s | small | p2 | t22 | -INF | 70 | 70 | -0.0079331
s | small | p2 | t23 | -INF | 70 | 70 | -0.0079212
s | small | p2 | t24 | -INF | 70 | 70 | -0.0079019
s | large | p1 | t1 | -INF | 70 | 70 | 0
s | large | p1 | t2 | -INF | 70 | 70 | 0
s | large | p1 | t3 | -INF | 49.9764 | 70 | 0
s | large | p1 | t4 | -INF | 70 | 70 | 0
s | large | p1 | t5 | -INF | 70 | 70 | 0
s | large | p1 | t6 | -INF | 70 | 70 | 0
s | large | p1 | t7 | -INF | 45.7421 | 70 | 0
s | large | p1 | t8 | -INF | 70 | 70 | 0
s | large | p1 | t9 | -INF | 37.489 | 70 | 0
s | large | p1 | t10 | -INF | 56.9632 | 70 | 0
s | large | p1 | t11 | -INF | 70 | 70 | 0
s | large | p1 | t12 | -INF | 70 | 70 | 0
s | large | p1 | t13 | -INF | 42.7552 | 70 | 0
s | large | p1 | t14 | -INF | 54.8091 | 70 | 0
s | large | p1 | t15 | -INF | 55.0776 | 70 | 0
s | large | p1 | t16 | -INF | 70 | 70 | 0
s | large | p1 | t17 | -INF | 70 | 70 | 0
s | large | p1 | t18 | -INF | 50.7732 | 70 | 0
s | large | p1 | t19 | -INF | 56.776 | 70 | 0
s | large | p1 | t20 | -INF | 70 | 70 | 0
s | large | p1 | t21 | -INF | 44.4552 | 70 | 0
s | large | p1 | t22 | -INF | 70 | 70 | 0
s | large | p1 | t23 | -INF | 70 | 70 | 0
s | large | p1 | t24 | -INF | 68.9979 | 70 | 0
s | large | p2 | t1 | -INF | 70 | 70 | 0
s | large | p2 | t2 | -INF | 70 | 70 | 0
s | large | p2 | t3 | -INF | 49.9764 | 70 | 0
s | large | p2 | t4 | -INF | 70 | 70 | 0
s | large | p2 | t5 | -INF | 66.7991 | 70 | 0
s | large | p2 | t6 | -INF | 70 | 70 | 0
s | large | p2 | t7 | -INF | 70 | 70 | 0
s | large | p2 | t8 | -INF | 61.2877 | 70 | 0
s | large | p2 | t9 | -INF | 40.4318 | 70 | 0
s | large | p2 | t10 | -INF | 38.8162 | 70 | 0
s | large | p2 | t11 | -INF | 49.9159 | 70 | 0
s | large | p2 | t12 | -INF | 42.8312 | 70 | 0
s | large | p2 | t13 | -INF | 54.7176 | 70 | 0
s | large | p2 | t14 | -INF | 70 | 70 | 0
s | large | p2 | t15 | -INF | 70 | 70 | 0
s | large | p2 | t16 | -INF | 44.4111 | 70 | 0
s | large | p2 | t17 | -INF | 48.437 | 70 | 0
s | large | p2 | t18 | -INF | 54.7315 | 70 | 0
s | large | p2 | t19 | -INF | 69.1736 | 70 | 0
s | large | p2 | t20 | -INF | 54.2901 | 70 | 0
s | large | p2 | t21 | -INF | 70 | 70 | 0
s | large | p2 | t22 | -INF | 48.6527 | 70 | 0
s | large | p2 | t23 | -INF | 46.4411 | 70 | 0
s | large | p2 | t24 | -INF | 44.3194 | 70 | 0
s | large | p3 | t1 | -INF | 49.2291 | 70 | 0
s | large | p3 | t2 | -INF | 46.979 | 70 | 0
s | large | p3 | t3 | -INF | 49.9764 | 70 | 0
s | large | p3 | t4 | -INF | 45.4849 | 70 | 0
s | large | p3 | t5 | -INF | 47.2233 | 70 | 0
s | large | p3 | t6 | -INF | 44.045 | 70 | 0
s | large | p3 | t7 | -INF | 44.0653 | 70 | 0
s | large | p3 | t8 | -INF | 43.7283 | 70 | 0
s | large | p3 | t9 | -INF | 37.489 | 70 | 0
s | large | p3 | t10 | -INF | 38.8162 | 70 | 0
s | large | p3 | t11 | -INF | 42.9041 | 70 | 0
s | large | p3 | t12 | -INF | 43.1111 | 70 | 0
s | large | p3 | t13 | -INF | 65.8001 | 70 | 0
s | large | p3 | t14 | -INF | 42.7409 | 70 | 0
s | large | p3 | t15 | -INF | 42.7266 | 70 | 0
s | large | p3 | t16 | -INF | 44.0485 | 70 | 0
s | large | p3 | t17 | -INF | 43.0989 | 70 | 0
s | large | p3 | t18 | -INF | 44.3721 | 70 | 0
s | large | p3 | t19 | -INF | 42.6857 | 70 | 0
s | large | p3 | t20 | -INF | 42.6783 | 70 | 0
s | large | p3 | t21 | -INF | 44.144 | 70 | 0
s | large | p3 | t22 | -INF | 43.0896 | 70 | 0
s | large | p3 | t23 | -INF | 43.4818 | 70 | 0
s | large | p3 | t24 | -INF | 44.3194 | 70 | 0
s | large | p4 | t1 | -INF | 43.6969 | 70 | 0
s | large | p4 | t2 | -INF | 44.0243 | 70 | 0
s | large | p4 | t3 | -INF | 70 | 70 | 0
s | large | p4 | t4 | -INF | 44.8061 | 70 | 0
s | large | p4 | t5 | -INF | 44.397 | 70 | 0
s | large | p4 | t6 | -INF | 46.5658 | 70 | 0
s | large | p4 | t7 | -INF | 70 | 70 | 0
s | large | p4 | t8 | -INF | 50.2094 | 70 | 0
s | large | p4 | t9 | -INF | 37.489 | 70 | 0
s | large | p4 | t10 | -INF | 38.8162 | 70 | 0
s | large | p4 | t11 | -INF | 42.9041 | 70 | 0
s | large | p4 | t12 | -INF | 49.4455 | 70 | 0
s | large | p4 | t13 | -INF | 42.9245 | 70 | 0
s | large | p4 | t14 | -INF | 42.7404 | 70 | 0
s | large | p4 | t15 | -INF | 42.7276 | 70 | 0
s | large | p4 | t16 | -INF | 44.0485 | 70 | 0
s | large | p4 | t17 | -INF | 43.0989 | 70 | 0
s | large | p4 | t18 | -INF | 44.3721 | 70 | 0
s | large | p4 | t19 | -INF | 42.6857 | 70 | 0
s | large | p4 | t20 | -INF | 42.7746 | 70 | 0
s | large | p4 | t21 | -INF | 44.144 | 70 | 0
s | large | p4 | t22 | -INF | 43.0896 | 70 | 0
s | large | p4 | t23 | -INF | 43.4818 | 70 | 0
s | large | p4 | t24 | -INF | 44.3194 | 70 | 0

## d
TOC
d | (set) | pump number
dim1
p1
p2
p3
p4

## Debit_s
TOC
Debit_s | (equation) | Equilibre des dÃ©bits Ã la source Ã (t)
t | Lowerbound | Value | Upperbound | Marginal
t1 | 0 | 7.1054e-14 | 0 | -0.0074347
t2 | 0 | -7.1054e-15 | 0 | -0.0074347
t3 | 0 | 5.6843e-14 | 0 | -0.0074347
t4 | 0 | 4.2633e-14 | 0 | -0.0074347
t5 | 0 | 3.5527e-14 | 0 | -0.0074347
t6 | 0 | 2.8422e-14 | 0 | -0.0074347
t7 | 0 | -5.6843e-14 | 0 | -0.0074347
t8 | 0 | 0 | 0 | -0.0074347
t9 | 0 | 4.2633e-14 | 0 | -0.011751
t10 | 0 | -1.7764e-14 | 0 | -0.011751
t11 | 0 | 2.8422e-14 | 0 | -0.011751
t12 | 0 | 5.6843e-14 | 0 | -0.011751
t13 | 0 | -1.4211e-14 | 0 | -0.011751
t14 | 0 | 4.5741e-14 | 0 | -0.011751
t15 | 0 | 3.5527e-15 | 0 | -0.011751
t16 | 0 | -2.8422e-14 | 0 | -0.011751
t17 | 0 | 8.5265e-14 | 0 | -0.011751
t18 | 0 | -1.4211e-14 | 0 | -0.011751
t19 | 0 | 0 | 0 | -0.011751
t20 | 0 | -4.2633e-14 | 0 | -0.011751
t21 | 0 | -2.8422e-14 | 0 | -0.011751
t22 | 0 | -1.4211e-14 | 0 | -0.011751
t23 | 0 | -1.4211e-14 | 0 | -0.011751
t24 | 0 | 2.8422e-14 | 0 | -0.011751

## degree
TOC
degree | (set) | polynomial degrees
dim1
0
1
2

## demand
TOC
demand | (parameter) | demand in water at each reservoir and each hour (m^3.h^-1)
r | t | Value
r12 | t1 | 9.67
r12 | t2 | 7
r12 | t3 | 4.33
r12 | t4 | 6
r12 | t5 | 6
r12 | t6 | 3.67
r12 | t7 | 2
r12 | t8 | 4
r12 | t9 | 3
r12 | t10 | 9.17
r12 | t11 | 13
r12 | t12 | 17
r12 | t13 | 21
r12 | t14 | 20.67
r12 | t15 | 20.17
r12 | t16 | 18
r12 | t17 | 15.83
r12 | t18 | 17.17
r12 | t19 | 13
r12 | t20 | 13.33
r12 | t21 | 19.5
r12 | t22 | 24.17
r12 | t23 | 22
r12 | t24 | 20
r13 | t1 | 0.83
r13 | t2 | 1.5
r13 | t3 | 1.17
r13 | t4 | 1.5
r13 | t5 | 1.83
r13 | t6 | 1.83
r13 | t7 | 1
r13 | t8 | 1
r13 | t10 | 3.5
r13 | t11 | 2
r13 | t12 | 3
r13 | t13 | 4
r13 | t14 | 3
r13 | t15 | 3
r13 | t16 | 3
r13 | t17 | 2
r13 | t18 | 3
r13 | t19 | 2
r13 | t20 | 2
r13 | t21 | 4
r13 | t22 | 3
r13 | t23 | 3
r13 | t24 | 3
r132 | t1 | 17.17
r132 | t2 | 19.5
r132 | t3 | 16.83
r132 | t4 | 7.67
r132 | t5 | 9
r132 | t6 | 9.67
r132 | t7 | 5.83
r132 | t8 | 11.67
r132 | t9 | 6.5
r132 | t10 | 17
r132 | t11 | 33.67
r132 | t12 | 41
r132 | t13 | 48
r132 | t14 | 37.5
r132 | t15 | 34.67
r132 | t16 | 35.83
r132 | t17 | 35
r132 | t18 | 36.33
r132 | t19 | 29.83
r132 | t20 | 31.5
r132 | t21 | 30.83
r132 | t22 | 37.17
r132 | t23 | 42.67
r132 | t24 | 35.33
r133 | t1 | 56.17
r133 | t2 | 59.33
r133 | t3 | 37.33
r133 | t4 | 31
r133 | t5 | 27
r133 | t6 | 26.33
r133 | t7 | 27
r133 | t8 | 26.5
r133 | t9 | 30.67
r133 | t10 | 45.67
r133 | t11 | 80.83
r133 | t12 | 113
r133 | t13 | 131.33
r133 | t14 | 116
r133 | t15 | 96.33
r133 | t16 | 75
r133 | t17 | 70
r133 | t18 | 65
r133 | t19 | 54
r133 | t20 | 52
r133 | t21 | 79
r133 | t22 | 120.17
r133 | t23 | 115
r133 | t24 | 78
r134 | t1 | 10.83
r134 | t2 | 6.83
r134 | t3 | 5
r134 | t4 | 4.17
r134 | t5 | 3
r134 | t6 | 5.5
r134 | t7 | 2
r134 | t8 | 1
r134 | t9 | 2
r134 | t10 | 6.83
r134 | t11 | 13
r134 | t12 | 19
r134 | t13 | 21
r134 | t14 | 16
r134 | t15 | 15
r134 | t16 | 13
r134 | t17 | 13
r134 | t18 | 6.5
r134 | t19 | 11.83
r134 | t20 | 8
r134 | t21 | 15
r134 | t22 | 20
r134 | t23 | 17
r134 | t24 | 10.67
r14 | t1 | 1.25
r14 | t10 | 4
r14 | t11 | 16
r14 | t12 | 14
r14 | t13 | 1
r14 | t14 | 5.25
r14 | t15 | 3.25
r14 | t16 | 5
r14 | t18 | 2
r14 | t19 | 3
r14 | t21 | 4.5
r14 | t22 | 4.25
r14 | t24 | 4
r15 | t1 | 19
r15 | t2 | 16
r15 | t3 | 8
r15 | t4 | 5
r15 | t5 | 4
r15 | t6 | 4.33
r15 | t7 | 6.33
r15 | t8 | 8.17
r15 | t9 | 6
r15 | t10 | 13
r15 | t11 | 34.67
r15 | t12 | 47
r15 | t13 | 49.17
r15 | t14 | 42.5
r15 | t15 | 37
r15 | t16 | 28.17
r15 | t17 | 31.33
r15 | t18 | 27
r15 | t19 | 23
r15 | t20 | 23
r15 | t21 | 31
r15 | t22 | 46
r15 | t23 | 36.17
r15 | t24 | 24
r151 | t1 | 47.67
r151 | t2 | 34.67
r151 | t3 | 15.33
r151 | t4 | 10.67
r151 | t5 | 10.83
r151 | t6 | 10
r151 | t7 | 10
r151 | t8 | 20.33
r151 | t9 | 18
r151 | t10 | 42.17
r151 | t11 | 96
r151 | t12 | 132
r151 | t13 | 140.5
r151 | t14 | 109
r151 | t15 | 85
r151 | t16 | 82
r151 | t17 | 73
r151 | t18 | 61
r151 | t19 | 58
r151 | t20 | 69
r151 | t21 | 111
r151 | t22 | 140
r151 | t23 | 103
r151 | t24 | 73.17
r16 | t1 | 13
r16 | t2 | 12
r16 | t3 | 10
r16 | t4 | 5
r16 | t5 | 2
r16 | t6 | 1
r16 | t7 | 2
r16 | t8 | 2
r16 | t9 | 2.17
r16 | t10 | 9.17
r16 | t11 | 10
r16 | t12 | 12
r16 | t13 | 13.33
r16 | t14 | 13.33
r16 | t15 | 14.17
r16 | t16 | 15
r16 | t17 | 13
r16 | t18 | 12
r16 | t19 | 13.17
r16 | t20 | 12.33
r16 | t21 | 13.17
r16 | t22 | 14
r16 | t23 | 13
r16 | t24 | 13.83
r161 | t1 | 47.33
r161 | t2 | 53
r161 | t3 | 51.83
r161 | t4 | 28
r161 | t5 | 25
r161 | t6 | 26.67
r161 | t7 | 21.67
r161 | t8 | 16.67
r161 | t9 | 4
r161 | t10 | 42.67
r161 | t11 | 60
r161 | t12 | 63
r161 | t13 | 110.83
r161 | t14 | 84.33
r161 | t15 | 93
r161 | t16 | 67
r161 | t17 | 73
r161 | t18 | 69
r161 | t19 | 56
r161 | t20 | 64
r161 | t21 | 89.5
r161 | t22 | 99
r161 | t23 | 95.83
r161 | t24 | 67
r17 | t1 | 25.17
r17 | t2 | 26.33
r17 | t3 | 10.83
r17 | t4 | 12
r17 | t5 | 12.17
r17 | t6 | 15
r17 | t7 | 13
r17 | t8 | 14
r17 | t9 | 5.67
r17 | t10 | 16.33
r17 | t11 | 42.67
r17 | t12 | 46
r17 | t13 | 56.67
r17 | t14 | 50.67
r17 | t15 | 46
r17 | t16 | 40
r17 | t17 | 34
r17 | t18 | 31
r17 | t19 | 30
r17 | t20 | 33
r17 | t21 | 36
r17 | t22 | 48.17
r17 | t23 | 45
r17 | t24 | 38
r171 | t1 | 10
r171 | t2 | 18.17
r171 | t3 | 13
r171 | t4 | 7.83
r171 | t5 | 4.67
r171 | t6 | 11
r171 | t7 | 6
r171 | t8 | 6
r171 | t9 | 7.5
r171 | t10 | 18
r171 | t11 | 39
r171 | t12 | 38
r171 | t13 | 40
r171 | t14 | 35
r171 | t15 | 33
r171 | t16 | 20
r171 | t17 | 23.83
r171 | t18 | 31
r171 | t19 | 23
r171 | t20 | 17.33
r171 | t21 | 26.67
r171 | t22 | 34.83
r171 | t23 | 21.5
r171 | t24 | 24
r18 | t1 | 8.33
r18 | t2 | 7.67
r18 | t3 | 5.83
r18 | t4 | 3
r18 | t5 | 3.33
r18 | t6 | 3
r18 | t7 | 4.5
r18 | t8 | 6.5
r18 | t9 | 11.17
r18 | t10 | 21.83
r18 | t11 | 26
r18 | t12 | 31
r18 | t13 | 27
r18 | t14 | 24
r18 | t15 | 21
r18 | t16 | 21
r18 | t17 | 16.83
r18 | t18 | 16.5
r18 | t19 | 17
r18 | t20 | 18.67
r18 | t21 | 23.33
r18 | t22 | 21.33
r18 | t23 | 19
r18 | t24 | 15
r181 | t1 | 125.67
r181 | t2 | 149.33
r181 | t3 | 128.67
r181 | t4 | 105.83
r181 | t5 | 93.33
r181 | t6 | 62.5
r181 | t7 | 41.5
r181 | t8 | 26.83
r181 | t9 | 23.33
r181 | t10 | 23.5
r181 | t11 | 21
r181 | t12 | 18
r181 | t13 | 18.33
r181 | t14 | 77.33
r181 | t15 | 137
r181 | t16 | 212.33
r181 | t17 | 200.83
r181 | t18 | 160.17
r181 | t19 | 131.17
r181 | t20 | 129
r181 | t21 | 117.67
r181 | t22 | 103.67
r181 | t23 | 96.17
r181 | t24 | 110.33
r19 | t1 | 60.5
r19 | t2 | 58.83
r19 | t3 | 51.83
r19 | t4 | 39.67
r19 | t5 | 31.33
r19 | t6 | 33
r19 | t7 | 24
r19 | t8 | 31.5
r19 | t9 | 43
r19 | t10 | 29
r19 | t11 | 89.5
r19 | t12 | 95.67
r19 | t13 | 94.83
r19 | t14 | 92.67
r19 | t15 | 83.5
r19 | t16 | 74.5
r19 | t17 | 65.83
r19 | t18 | 70.67
r19 | t19 | 65.5
r19 | t20 | 68.33
r19 | t21 | 78.33
r19 | t22 | 94.33
r19 | t23 | 90.5
r19 | t24 | 81.67
r191 | t1 | 13.75
r191 | t2 | 4.75
r191 | t3 | 25.75
r191 | t4 | 18
r191 | t5 | 15
r191 | t6 | 14
r191 | t8 | 28.25
r191 | t9 | 44
r191 | t10 | 78
r191 | t11 | 122
r191 | t12 | 102
r191 | t13 | 87
r191 | t14 | 81
r191 | t15 | 62
r191 | t16 | 94.75
r191 | t17 | 71
r191 | t18 | 17
r191 | t19 | 37.75
r191 | t20 | 99
r191 | t21 | 117.25
r191 | t22 | 92.75
r191 | t23 | 63
r191 | t24 | 54.25

## Elec_pompe
TOC
Elec_pompe | (equation) | Consommation Ã©lectrique de la pompe (k) Ã (t)
c | d | t | Lowerbound | Value | Upperbound | Marginal
small | p1 | t1 | 0 | 0 | INF | 0.02916
small | p1 | t2 | 0 | 0 | INF | 0.02916
small | p1 | t3 | 0 | 0 | INF | 0.02916
small | p1 | t4 | 0 | 0 | INF | 0.02916
small | p1 | t5 | 0 | 0 | INF | 0.02916
small | p1 | t6 | 0 | 0 | INF | 0.02916
small | p1 | t7 | 0 | 0 | INF | 0.02916
small | p1 | t8 | 0 | 0 | INF | 0.02916
small | p1 | t9 | 0 | 0 | INF | 0.04609
small | p1 | t10 | 0 | 0 | INF | 0.04609
small | p1 | t11 | 0 | 0 | INF | 0.04609
small | p1 | t12 | 0 | 0 | INF | 0.04609
small | p1 | t13 | 0 | 0 | INF | 0.04609
small | p1 | t14 | 0 | 0 | INF | 0.04609
small | p1 | t15 | 0 | 0 | INF | 0.04609
small | p1 | t16 | 0 | 0 | INF | 0.04609
small | p1 | t17 | 0 | 0 | INF | 0.04609
small | p1 | t18 | 0 | 0 | INF | 0.04609
small | p1 | t19 | 0 | 0 | INF | 0.04609
small | p1 | t20 | 0 | 0 | INF | 0.04609
small | p1 | t21 | 0 | 0 | INF | 0.04609
small | p1 | t22 | 0 | 0 | INF | 0.04609
small | p1 | t23 | 0 | 0 | INF | 0.04609
small | p1 | t24 | 0 | 0 | INF | 0.04609
small | p2 | t1 | 0 | 0 | INF | 0.02916
small | p2 | t2 | 0 | 0 | INF | 0.02916
small | p2 | t3 | 0 | 0 | INF | 0.02916
small | p2 | t4 | 0 | 0 | INF | 0.02916
small | p2 | t5 | 0 | 0 | INF | 0.02916
small | p2 | t6 | 0 | 0 | INF | 0.02916
small | p2 | t7 | 0 | 0 | INF | 0.02916
small | p2 | t8 | 0 | 0 | INF | 0.02916
small | p2 | t9 | 0 | 0 | INF | 0.04609
small | p2 | t10 | 0 | 0 | INF | 0.04609
small | p2 | t11 | 0 | 0 | INF | 0.04609
small | p2 | t12 | 0 | 0 | INF | 0.04609
small | p2 | t13 | 0 | 0 | INF | 0.04609
small | p2 | t14 | 0 | 0 | INF | 0.04609
small | p2 | t15 | 0 | 0 | INF | 0.04609
small | p2 | t16 | 0 | 0 | INF | 0.04609
small | p2 | t17 | 0 | 0 | INF | 0.04609
small | p2 | t18 | 0 | 0 | INF | 0.04609
small | p2 | t19 | 0 | 0 | INF | 0.04609
small | p2 | t20 | 0 | 0 | INF | 0.04609
small | p2 | t21 | 0 | 0 | INF | 0.04609
small | p2 | t22 | 0 | 0 | INF | 0.04609
small | p2 | t23 | 0 | 0 | INF | 0.04609
small | p2 | t24 | 0 | 0 | INF | 0.04609
large | p1 | t1 | 0 | 1.4211e-14 | INF | 0.02916
large | p1 | t2 | 0 | 1.4211e-14 | INF | 0.02916
large | p1 | t3 | 0 | 0 | INF | 0.02916
large | p1 | t4 | 0 | 1.4211e-14 | INF | 0.02916
large | p1 | t5 | 0 | 1.4211e-14 | INF | 0.02916
large | p1 | t6 | 0 | 0 | INF | 0.02916
large | p1 | t7 | 0 | 0 | INF | 0.02916
large | p1 | t8 | 0 | -1.4211e-14 | INF | 0.02916
large | p1 | t9 | 0 | 0 | INF | 0.04609
large | p1 | t10 | 0 | 1.4211e-14 | INF | 0.04609
large | p1 | t11 | 0 | 0 | INF | 0.04609
large | p1 | t12 | 0 | 0 | INF | 0.04609
large | p1 | t13 | 0 | 0 | INF | 0.04609
large | p1 | t14 | 0 | 0 | INF | 0.04609
large | p1 | t15 | 0 | 0 | INF | 0.04609
large | p1 | t16 | 0 | 0 | INF | 0.04609
large | p1 | t17 | 0 | 0 | INF | 0.04609
large | p1 | t18 | 0 | -1.4211e-14 | INF | 0.04609
large | p1 | t19 | 0 | 0 | INF | 0.04609
large | p1 | t20 | 0 | 0 | INF | 0.04609
large | p1 | t21 | 0 | -1.4211e-14 | INF | 0.04609
large | p1 | t22 | 0 | -1.4211e-14 | INF | 0.04609
large | p1 | t23 | 0 | 1.4211e-14 | INF | 0.04609
large | p1 | t24 | 0 | 0 | INF | 0.04609
large | p2 | t1 | 0 | 1.4211e-14 | INF | 0.02916
large | p2 | t2 | 0 | 1.4211e-14 | INF | 0.02916
large | p2 | t3 | 0 | 1.4211e-14 | INF | 0.02916
large | p2 | t4 | 0 | 1.4211e-14 | INF | 0.02916
large | p2 | t5 | 0 | -1.4211e-14 | INF | 0.02916
large | p2 | t6 | 0 | 0 | INF | 0.02916
large | p2 | t7 | 0 | 0 | INF | 0.02916
large | p2 | t8 | 0 | 1.4211e-14 | INF | 0.02916
large | p2 | t9 | 0 | 0 | INF | 0.04609
large | p2 | t10 | 0 | 0 | INF | 0.04609
large | p2 | t11 | 0 | 0 | INF | 0.04609
large | p2 | t12 | 0 | 0 | INF | 0.04609
large | p2 | t13 | 0 | 1.4211e-14 | INF | 0.04609
large | p2 | t14 | 0 | -1.4211e-14 | INF | 0.04609
large | p2 | t15 | 0 | 0 | INF | 0.04609
large | p2 | t16 | 0 | 0 | INF | 0.04609
large | p2 | t17 | 0 | 0 | INF | 0.04609
large | p2 | t18 | 0 | 1.4211e-14 | INF | 0.04609
large | p2 | t19 | 0 | -1.4211e-14 | INF | 0.04609
large | p2 | t20 | 0 | 0 | INF | 0.04609
large | p2 | t21 | 0 | 0 | INF | 0.04609
large | p2 | t22 | 0 | 1.4211e-14 | INF | 0.04609
large | p2 | t23 | 0 | 0 | INF | 0.04609
large | p2 | t24 | 0 | 0 | INF | 0.04609
large | p3 | t1 | 0 | 0 | INF | 0.02916
large | p3 | t2 | 0 | 0 | INF | 0.02916
large | p3 | t3 | 0 | 1.4211e-14 | INF | 0.02916
large | p3 | t4 | 0 | 0 | INF | 0.02916
large | p3 | t5 | 0 | 0 | INF | 0.02916
large | p3 | t6 | 0 | 0 | INF | 0.02916
large | p3 | t7 | 0 | 0 | INF | 0.02916
large | p3 | t8 | 0 | 0 | INF | 0.02916
large | p3 | t9 | 0 | 0 | INF | 0.04609
large | p3 | t10 | 0 | 0 | INF | 0.04609
large | p3 | t11 | 0 | 0 | INF | 0.04609
large | p3 | t12 | 0 | 0 | INF | 0.04609
large | p3 | t13 | 0 | 1.4211e-14 | INF | 0.04609
large | p3 | t14 | 0 | 0 | INF | 0.04609
large | p3 | t15 | 0 | 0 | INF | 0.04609
large | p3 | t16 | 0 | 0 | INF | 0.04609
large | p3 | t17 | 0 | -1.4211e-14 | INF | 0.04609
large | p3 | t18 | 0 | 0 | INF | 0.04609
large | p3 | t19 | 0 | 0 | INF | 0.04609
large | p3 | t20 | 0 | 0 | INF | 0.04609
large | p3 | t21 | 0 | -1.4211e-14 | INF | 0.04609
large | p3 | t22 | 0 | 0 | INF | 0.04609
large | p3 | t23 | 0 | 0 | INF | 0.04609
large | p3 | t24 | 0 | 0 | INF | 0.04609
large | p4 | t1 | 0 | 0 | INF | 0.02916
large | p4 | t2 | 0 | 0 | INF | 0.02916
large | p4 | t3 | 0 | 0 | INF | 0.02916
large | p4 | t4 | 0 | 0 | INF | 0.02916
large | p4 | t5 | 0 | 1.4211e-14 | INF | 0.02916
large | p4 | t6 | 0 | 0 | INF | 0.02916
large | p4 | t7 | 0 | 0 | INF | 0.02916
large | p4 | t8 | 0 | -1.4211e-14 | INF | 0.02916
large | p4 | t9 | 0 | 0 | INF | 0.04609
large | p4 | t10 | 0 | 0 | INF | 0.04609
large | p4 | t11 | 0 | 0 | INF | 0.04609
large | p4 | t12 | 0 | 0 | INF | 0.04609
large | p4 | t13 | 0 | 0 | INF | 0.04609
large | p4 | t14 | 0 | 0 | INF | 0.04609
large | p4 | t15 | 0 | 0 | INF | 0.04609
large | p4 | t16 | 0 | 0 | INF | 0.04609
large | p4 | t17 | 0 | -1.4211e-14 | INF | 0.04609
large | p4 | t18 | 0 | 0 | INF | 0.04609
large | p4 | t19 | 0 | 0 | INF | 0.04609
large | p4 | t20 | 0 | -1.4211e-14 | INF | 0.04609
large | p4 | t21 | 0 | -1.4211e-14 | INF | 0.04609
large | p4 | t22 | 0 | 0 | INF | 0.04609
large | p4 | t23 | 0 | 0 | INF | 0.04609
large | p4 | t24 | 0 | 0 | INF | 0.04609

## gamma
TOC
gamma | (parameter) | linear fit of the electrical power (kW) on the flow (m^3.h^-1) for each class of pumps
c | degree | Value
small | 0 | 35.3817
small | 1 | 0.24236
large | 0 | 77.1244
large | 1 | 0.25496

## height
TOC
height | (parameter) | elevation at each node relative to s (m)
n | Value
s | 40
j39 | 68
j14 | 63
j16 | 87
j17 | 99
j19 | 110
j21 | 102
j24 | 87
j26 | 87
j27 | 88
j30 | 48
j2 | 74
j3 | 75
j6 | 56
j7 | 64
j10 | 73
r12 | 91
r13 | 116
r132 | 100
r133 | 81
r134 | 131
r14 | 97
r15 | 61
r151 | 91
r16 | 106
r161 | 93
r17 | 92
r171 | 80
r18 | 86
r181 | 91
r19 | 75
r191 | 87

## j
TOC
j | (set) | junctions
n
j39
j14
j16
j17
j19
j21
j24
j26
j27
j30
j2
j3
j6
j7
j10

## k
TOC
k | (set) | pumps
c | d
small | p1
small | p2
large | p1
large | p2
large | p3
large | p4

## l
TOC
l | (set) | pipes
n | n
s | j39
j39 | j14
j39 | j2
j14 | j16
j14 | r12
j16 | j17
j16 | j24
j17 | j19
j17 | r13
j19 | j21
j19 | r132
j21 | r133
j21 | r134
j24 | j26
j24 | r14
j26 | j27
j26 | j30
j27 | r16
j27 | r161
j30 | r15
j30 | r151
j2 | j3
j2 | j6
j3 | r17
j3 | r171
j6 | j7
j6 | j10
j7 | r19
j7 | r191
j10 | r18
j10 | r181

## n
TOC
n | (set) | nodes
dim1
s
j39
j14
j16
j17
j19
j21
j24
j26
j27
j30
j2
j3
j6
j7
j10
r12
r13
r132
r133
r134
r14
r15
r151
r16
r161
r17
r171
r18
r181
r19
r191

## night
TOC
night | (set) | night periods
t
t1
t2
t3
t4
t5
t6
t7
t8

## Noeud
TOC
Noeud | (equation) | Contrainte dÃ©bit noeud (n) Ã (t)
n | t | Lowerbound | Value | Upperbound | Marginal
j39 | t1 | 0 | 0 | 0 | -0.0076129
j39 | t2 | 0 | -5.6843e-14 | 0 | -0.0076129
j39 | t3 | 0 | -5.6843e-14 | 0 | -0.0076129
j39 | t4 | 0 | -5.6843e-14 | 0 | -0.0076129
j39 | t5 | 0 | -5.6843e-14 | 0 | -0.0076129
j39 | t6 | 0 | 0 | 0 | -0.0076129
j39 | t7 | 0 | 0 | 0 | -0.0076129
j39 | t8 | 0 | 0 | 0 | -0.0076129
j39 | t9 | 0 | 0 | 0 | -0.011773
j39 | t10 | 0 | 2.8422e-14 | 0 | -0.011789
j39 | t11 | 0 | 0 | 0 | -0.011853
j39 | t12 | 0 | -2.8422e-14 | 0 | -0.011853
j39 | t13 | 0 | 0 | 0 | -0.011853
j39 | t14 | 0 | 2.8422e-14 | 0 | -0.011853
j39 | t15 | 0 | 2.8422e-14 | 0 | -0.011853
j39 | t16 | 0 | 2.8422e-14 | 0 | -0.011853
j39 | t17 | 0 | -2.8422e-14 | 0 | -0.011853
j39 | t18 | 0 | 0 | 0 | -0.011853
j39 | t19 | 0 | -2.8422e-14 | 0 | -0.011853
j39 | t20 | 0 | 0 | 0 | -0.011853
j39 | t21 | 0 | 0 | 0 | -0.011853
j39 | t22 | 0 | -2.8422e-14 | 0 | -0.011853
j39 | t23 | 0 | 0 | 0 | -0.011853
j39 | t24 | 0 | -5.6843e-14 | 0 | -0.011853
j14 | t1 | 0 | -3.1974e-14 | 0 | -0.0079901
j14 | t2 | 0 | 4.9738e-14 | 0 | -0.0079901
j14 | t3 | 0 | 1.7764e-14 | 0 | -0.0079901
j14 | t4 | 0 | 4.2633e-14 | 0 | -0.0079901
j14 | t5 | 0 | -7.1054e-15 | 0 | -0.0079901
j14 | t6 | 0 | -3.5527e-15 | 0 | -0.0079901
j14 | t7 | 0 | 3.908e-14 | 0 | -0.0079901
j14 | t8 | 0 | -1.7764e-15 | 0 | -0.0079901
j14 | t9 | 0 | 1.4211e-14 | 0 | -0.011823
j14 | t10 | 0 | -1.2434e-14 | 0 | -0.011887
j14 | t11 | 0 | -1.2434e-14 | 0 | -0.012132
j14 | t12 | 0 | -2.3093e-14 | 0 | -0.012132
j14 | t13 | 0 | 2.1316e-14 | 0 | -0.012132
j14 | t14 | 0 | 1.2434e-14 | 0 | -0.012132
j14 | t15 | 0 | -4.7962e-14 | 0 | -0.012132
j14 | t16 | 0 | -3.5527e-15 | 0 | -0.012132
j14 | t17 | 0 | -2.1316e-14 | 0 | -0.012132
j14 | t18 | 0 | 5.3291e-15 | 0 | -0.012132
j14 | t19 | 0 | -4.6185e-14 | 0 | -0.012132
j14 | t20 | 0 | 8.8818e-15 | 0 | -0.012132
j14 | t21 | 0 | -8.8818e-15 | 0 | -0.012132
j14 | t22 | 0 | -3.5527e-15 | 0 | -0.012132
j14 | t23 | 0 | 3.908e-14 | 0 | -0.012132
j14 | t24 | 0 | 0 | 0 | -0.012132
j16 | t1 | 0 | 2.8422e-14 | 0 | -0.0082976
j16 | t2 | 0 | -5.6843e-14 | 0 | -0.0082976
j16 | t3 | 0 | -2.8422e-14 | 0 | -0.0082976
j16 | t4 | 0 | -2.8422e-14 | 0 | -0.0082976
j16 | t5 | 0 | 0 | 0 | -0.0082976
j16 | t6 | 0 | 0 | 0 | -0.0082976
j16 | t7 | 0 | -5.6843e-14 | 0 | -0.0082976
j16 | t8 | 0 | 2.8422e-14 | 0 | -0.0082976
j16 | t9 | 0 | 0 | 0 | -0.011866
j16 | t10 | 0 | 0 | 0 | -0.011968
j16 | t11 | 0 | 0 | 0 | -0.012364
j16 | t12 | 0 | 0 | 0 | -0.012364
j16 | t13 | 0 | 0 | 0 | -0.012364
j16 | t14 | 0 | 0 | 0 | -0.012364
j16 | t15 | 0 | 2.8422e-14 | 0 | -0.012364
j16 | t16 | 0 | 0 | 0 | -0.012364
j16 | t17 | 0 | 0 | 0 | -0.012364
j16 | t18 | 0 | 0 | 0 | -0.012364
j16 | t19 | 0 | 2.8422e-14 | 0 | -0.012364
j16 | t20 | 0 | -2.8422e-14 | 0 | -0.012364
j16 | t21 | 0 | 0 | 0 | -0.012364
j16 | t22 | 0 | 2.8422e-14 | 0 | -0.012364
j16 | t23 | 0 | -5.6843e-14 | 0 | -0.012364
j16 | t24 | 0 | 2.8422e-14 | 0 | -0.012364
j17 | t1 | 0 | -3.5527e-15 | 0 | -0.0088109
j17 | t2 | 0 | 5.3291e-15 | 0 | -0.0088109
j17 | t3 | 0 | -2.6645e-15 | 0 | -0.0088109
j17 | t4 | 0 | 1.7764e-15 | 0 | -0.0088109
j17 | t5 | 0 | 2.6645e-15 | 0 | -0.0088109
j17 | t6 | 0 | -2.6645e-15 | 0 | -0.0088109
j17 | t7 | 0 | 0 | 0 | -0.0088109
j17 | t8 | 0 | 5.3291e-15 | 0 | -0.0088109
j17 | t9 | 0 | 0 | 0 | -0.011986
j17 | t10 | 0 | 0 | 0 | -0.012107
j17 | t11 | 0 | 0 | 0 | -0.012702
j17 | t12 | 0 | 0 | 0 | -0.012702
j17 | t13 | 0 | 0 | 0 | -0.012702
j17 | t14 | 0 | 0 | 0 | -0.012702
j17 | t15 | 0 | 0 | 0 | -0.012702
j17 | t16 | 0 | 0 | 0 | -0.012702
j17 | t17 | 0 | 0 | 0 | -0.012702
j17 | t18 | 0 | 0 | 0 | -0.012702
j17 | t19 | 0 | 0 | 0 | -0.012702
j17 | t20 | 0 | 0 | 0 | -0.012702
j17 | t21 | 0 | 0 | 0 | -0.012702
j17 | t22 | 0 | 0 | 0 | -0.012702
j17 | t23 | 0 | 0 | 0 | -0.012702
j17 | t24 | 0 | 0 | 0 | -0.012702
j19 | t1 | 0 | 0 | 0 | -0.01018
j19 | t2 | 0 | 0 | 0 | -0.01018
j19 | t3 | 0 | -7.1054e-15 | 0 | -0.01018
j19 | t4 | 0 | -7.1054e-15 | 0 | -0.01018
j19 | t5 | 0 | 0 | 0 | -0.01018
j19 | t6 | 0 | 7.1054e-15 | 0 | -0.01018
j19 | t7 | 0 | 7.1054e-15 | 0 | -0.01018
j19 | t8 | 0 | -1.0658e-14 | 0 | -0.01018
j19 | t9 | 0 | 0 | 0 | -0.012322
j19 | t10 | 0 | 2.8422e-14 | 0 | -0.012498
j19 | t11 | 0 | 0 | 0 | -0.013657
j19 | t12 | 0 | -3.5527e-15 | 0 | -0.013657
j19 | t13 | 0 | 0 | 0 | -0.013657
j19 | t14 | 0 | 3.5527e-15 | 0 | -0.013657
j19 | t15 | 0 | -3.5527e-15 | 0 | -0.013657
j19 | t16 | 0 | 1.0658e-14 | 0 | -0.013657
j19 | t17 | 0 | 7.1054e-15 | 0 | -0.013657
j19 | t18 | 0 | -3.5527e-15 | 0 | -0.013657
j19 | t19 | 0 | 3.5527e-15 | 0 | -0.013657
j19 | t20 | 0 | 0 | 0 | -0.013657
j19 | t21 | 0 | 0 | 0 | -0.013657
j19 | t22 | 0 | -7.1054e-15 | 0 | -0.013657
j19 | t23 | 0 | 0 | 0 | -0.013657
j19 | t24 | 0 | 7.1054e-15 | 0 | -0.013657
j21 | t1 | 0 | 5.4001e-13 | 0 | -0.012089
j21 | t2 | 0 | -4.4409e-15 | 0 | -0.012089
j21 | t3 | 0 | 2.8422e-14 | 0 | -0.012089
j21 | t4 | 0 | 7.1054e-15 | 0 | -0.012089
j21 | t5 | 0 | 1.4211e-14 | 0 | -0.012089
j21 | t6 | 0 | -3.5527e-15 | 0 | -0.012089
j21 | t7 | 0 | 0 | 0 | -0.012089
j21 | t8 | 0 | 7.1054e-15 | 0 | -0.0121
j21 | t9 | 0 | 0 | 0 | -0.012944
j21 | t10 | 0 | -7.1054e-15 | 0 | -0.013128
j21 | t11 | 0 | 0 | 0 | -0.015134
j21 | t12 | 0 | 0 | 0 | -0.015134
j21 | t13 | 0 | 0 | 0 | -0.015134
j21 | t14 | 0 | 0 | 0 | -0.015134
j21 | t15 | 0 | 0 | 0 | -0.015134
j21 | t16 | 0 | 0 | 0 | -0.015134
j21 | t17 | 0 | 0 | 0 | -0.015134
j21 | t18 | 0 | 0 | 0 | -0.015134
j21 | t19 | 0 | 0 | 0 | -0.015134
j21 | t20 | 0 | 0 | 0 | -0.015134
j21 | t21 | 0 | -5.3291e-15 | 0 | -0.015134
j21 | t22 | 0 | -1.4211e-14 | 0 | -0.015134
j21 | t23 | 0 | 0 | 0 | -0.015134
j21 | t24 | 0 | -7.1054e-15 | 0 | -0.015134
j24 | t1 | 0 | 0 | 0 | -0.0082976
j24 | t2 | 0 | 0 | 0 | -0.0082976
j24 | t3 | 0 | 0 | 0 | -0.0082976
j24 | t4 | 0 | 0 | 0 | -0.0082976
j24 | t5 | 0 | 3.5527e-15 | 0 | -0.0082976
j24 | t6 | 0 | -1.7764e-15 | 0 | -0.0082976
j24 | t7 | 0 | 0 | 0 | -0.0082976
j24 | t8 | 0 | 1.7764e-15 | 0 | -0.0082976
j24 | t9 | 0 | 0 | 0 | -0.011866
j24 | t10 | 0 | 0 | 0 | -0.011968
j24 | t11 | 0 | 0 | 0 | -0.012364
j24 | t12 | 0 | 0 | 0 | -0.012364
j24 | t13 | 0 | 0 | 0 | -0.012364
j24 | t14 | 0 | 0 | 0 | -0.012364
j24 | t15 | 0 | -1.2434e-14 | 0 | -0.012364
j24 | t16 | 0 | 0 | 0 | -0.012364
j24 | t17 | 0 | 0 | 0 | -0.012364
j24 | t18 | 0 | 0 | 0 | -0.012364
j24 | t19 | 0 | 0 | 0 | -0.012364
j24 | t20 | 0 | 0 | 0 | -0.012364
j24 | t21 | 0 | 0 | 0 | -0.012364
j24 | t22 | 0 | 0 | 0 | -0.012364
j24 | t23 | 0 | 0 | 0 | -0.012364
j24 | t24 | 0 | -1.4211e-14 | 0 | -0.012364
j26 | t1 | 0 | 0 | 0 | -0.0082976
j26 | t2 | 0 | 0 | 0 | -0.0082976
j26 | t3 | 0 | -1.0658e-14 | 0 | -0.0082976
j26 | t4 | 0 | 0 | 0 | -0.0082976
j26 | t5 | 0 | 0 | 0 | -0.0082976
j26 | t6 | 0 | 0 | 0 | -0.0082976
j26 | t7 | 0 | 0 | 0 | -0.0082976
j26 | t8 | 0 | -1.4211e-14 | 0 | -0.0082976
j26 | t9 | 0 | -7.1054e-14 | 0 | -0.011866
j26 | t10 | 0 | 7.1054e-15 | 0 | -0.011968
j26 | t11 | 0 | 0 | 0 | -0.012364
j26 | t12 | 0 | 0 | 0 | -0.012364
j26 | t13 | 0 | 0 | 0 | -0.012364
j26 | t14 | 0 | -1.4211e-14 | 0 | -0.012364
j26 | t15 | 0 | 0 | 0 | -0.012364
j26 | t16 | 0 | 0 | 0 | -0.012364
j26 | t17 | 0 | 0 | 0 | -0.012364
j26 | t18 | 0 | -2.8422e-14 | 0 | -0.012364
j26 | t19 | 0 | 0 | 0 | -0.012364
j26 | t20 | 0 | 0 | 0 | -0.012364
j26 | t21 | 0 | 0 | 0 | -0.012364
j26 | t22 | 0 | -7.1054e-15 | 0 | -0.012364
j26 | t23 | 0 | 1.4211e-14 | 0 | -0.012364
j26 | t24 | 0 | 0 | 0 | -0.012364
j27 | t1 | 0 | 0 | 0 | -0.0082976
j27 | t2 | 0 | 0 | 0 | -0.0082976
j27 | t3 | 0 | 0 | 0 | -0.0082976
j27 | t4 | 0 | 0 | 0 | -0.0082976
j27 | t5 | 0 | 0 | 0 | -0.0082976
j27 | t6 | 0 | 0 | 0 | -0.0082976
j27 | t7 | 0 | 0 | 0 | -0.0082976
j27 | t8 | 0 | 1.0658e-14 | 0 | -0.0082976
j27 | t9 | 0 | 4.2633e-14 | 0 | -0.011866
j27 | t10 | 0 | 0 | 0 | -0.011968
j27 | t11 | 0 | 0 | 0 | -0.012364
j27 | t12 | 0 | 0 | 0 | -0.012364
j27 | t13 | 0 | 0 | 0 | -0.012364
j27 | t14 | 0 | 0 | 0 | -0.012364
j27 | t15 | 0 | 0 | 0 | -0.012364
j27 | t16 | 0 | 0 | 0 | -0.012364
j27 | t17 | 0 | 0 | 0 | -0.012364
j27 | t18 | 0 | 0 | 0 | -0.012364
j27 | t19 | 0 | 0 | 0 | -0.012364
j27 | t20 | 0 | 2.8422e-14 | 0 | -0.012364
j27 | t21 | 0 | 0 | 0 | -0.012364
j27 | t22 | 0 | 0 | 0 | -0.012364
j27 | t23 | 0 | 0 | 0 | -0.012364
j27 | t24 | 0 | 0 | 0 | -0.012364
j30 | t1 | 0 | 0 | 0 | -0.0082976
j30 | t2 | 0 | 3.5527e-15 | 0 | -0.0082976
j30 | t3 | 0 | 0 | 0 | -0.0082976
j30 | t4 | 0 | 0 | 0 | -0.0082976
j30 | t5 | 0 | 0 | 0 | -0.0082976
j30 | t6 | 0 | 0 | 0 | -0.0082976
j30 | t7 | 0 | 0 | 0 | -0.0082976
j30 | t8 | 0 | 0 | 0 | -0.0082976
j30 | t9 | 0 | 0 | 0 | -0.011866
j30 | t10 | 0 | -7.1054e-15 | 0 | -0.011968
j30 | t11 | 0 | 2.8422e-14 | 0 | -0.012364
j30 | t12 | 0 | 2.8422e-14 | 0 | -0.012364
j30 | t13 | 0 | 0 | 0 | -0.012364
j30 | t14 | 0 | 5.3291e-15 | 0 | -0.012364
j30 | t15 | 0 | 7.1054e-15 | 0 | -0.012364
j30 | t16 | 0 | 0 | 0 | -0.012364
j30 | t17 | 0 | 0 | 0 | -0.012364
j30 | t18 | 0 | 1.4211e-14 | 0 | -0.012364
j30 | t19 | 0 | 0 | 0 | -0.012364
j30 | t20 | 0 | 0 | 0 | -0.012364
j30 | t21 | 0 | -7.1054e-15 | 0 | -0.012364
j30 | t22 | 0 | 0 | 0 | -0.012364
j30 | t23 | 0 | 0 | 0 | -0.012364
j30 | t24 | 0 | 0 | 0 | -0.012364
j2 | t1 | 0 | 0 | 0 | -0.0076129
j2 | t2 | 0 | 0 | 0 | -0.0076129
j2 | t3 | 0 | 0 | 0 | -0.0076129
j2 | t4 | 0 | 5.6843e-14 | 0 | -0.0076129
j2 | t5 | 0 | 0 | 0 | -0.0076129
j2 | t6 | 0 | 0 | 0 | -0.0076129
j2 | t7 | 0 | 0 | 0 | -0.0076129
j2 | t8 | 0 | 0 | 0 | -0.0076129
j2 | t9 | 0 | -1.4211e-14 | 0 | -0.011773
j2 | t10 | 0 | 0 | 0 | -0.011789
j2 | t11 | 0 | 0 | 0 | -0.011853
j2 | t12 | 0 | 1.4211e-14 | 0 | -0.011853
j2 | t13 | 0 | 0 | 0 | -0.011853
j2 | t14 | 0 | -2.8422e-14 | 0 | -0.011853
j2 | t15 | 0 | 0 | 0 | -0.011853
j2 | t16 | 0 | 0 | 0 | -0.011853
j2 | t17 | 0 | -1.4211e-14 | 0 | -0.011853
j2 | t18 | 0 | 0 | 0 | -0.011853
j2 | t19 | 0 | 0 | 0 | -0.011853
j2 | t20 | 0 | 0 | 0 | -0.011853
j2 | t21 | 0 | 0 | 0 | -0.011853
j2 | t22 | 0 | 0 | 0 | -0.011853
j2 | t23 | 0 | 0 | 0 | -0.011853
j2 | t24 | 0 | 0 | 0 | -0.011853
j3 | t1 | 0 | -2.8422e-14 | 0 | -0.0076129
j3 | t2 | 0 | 0 | 0 | -0.0076129
j3 | t3 | 0 | 7.1054e-15 | 0 | -0.0076129
j3 | t4 | 0 | 0 | 0 | -0.0076129
j3 | t5 | 0 | 0 | 0 | -0.0076129
j3 | t6 | 0 | 0 | 0 | -0.0076129
j3 | t7 | 0 | 0 | 0 | -0.0076129
j3 | t8 | 0 | 0 | 0 | -0.0076129
j3 | t9 | 0 | 0 | 0 | -0.011773
j3 | t10 | 0 | -1.4211e-14 | 0 | -0.011789
j3 | t11 | 0 | 0 | 0 | -0.011853
j3 | t12 | 0 | 0 | 0 | -0.011853
j3 | t13 | 0 | 0 | 0 | -0.011853
j3 | t14 | 0 | -3.5527e-15 | 0 | -0.011853
j3 | t15 | 0 | 0 | 0 | -0.011853
j3 | t16 | 0 | 0 | 0 | -0.011853
j3 | t17 | 0 | 0 | 0 | -0.011853
j3 | t18 | 0 | 0 | 0 | -0.011853
j3 | t19 | 0 | 0 | 0 | -0.011853
j3 | t20 | 0 | 0 | 0 | -0.011853
j3 | t21 | 0 | 0 | 0 | -0.011853
j3 | t22 | 0 | 0 | 0 | -0.011853
j3 | t23 | 0 | 0 | 0 | -0.011853
j3 | t24 | 0 | 0 | 0 | -0.011853
j6 | t1 | 0 | -2.8422e-14 | 0 | -0.0076129
j6 | t2 | 0 | 0 | 0 | -0.0076129
j6 | t3 | 0 | 0 | 0 | -0.0076129
j6 | t4 | 0 | 0 | 0 | -0.0076129
j6 | t5 | 0 | 2.8422e-14 | 0 | -0.0076129
j6 | t6 | 0 | -2.8422e-14 | 0 | -0.0076129
j6 | t7 | 0 | -2.8422e-14 | 0 | -0.0076129
j6 | t8 | 0 | -1.4211e-14 | 0 | -0.0076129
j6 | t9 | 0 | 4.2633e-14 | 0 | -0.011773
j6 | t10 | 0 | 9.2371e-14 | 0 | -0.011789
j6 | t11 | 0 | 0 | 0 | -0.011853
j6 | t12 | 0 | 0 | 0 | -0.011853
j6 | t13 | 0 | 7.1054e-15 | 0 | -0.011853
j6 | t14 | 0 | 0 | 0 | -0.011853
j6 | t15 | 0 | 7.1054e-15 | 0 | -0.011853
j6 | t16 | 0 | 0 | 0 | -0.011853
j6 | t17 | 0 | 0 | 0 | -0.011853
j6 | t18 | 0 | 0 | 0 | -0.011853
j6 | t19 | 0 | 1.4211e-14 | 0 | -0.011853
j6 | t20 | 0 | 0 | 0 | -0.011853
j6 | t21 | 0 | 1.4211e-14 | 0 | -0.011853
j6 | t22 | 0 | 0 | 0 | -0.011853
j6 | t23 | 0 | -2.8422e-14 | 0 | -0.011853
j6 | t24 | 0 | 1.4211e-14 | 0 | -0.011853
j7 | t1 | 0 | 0 | 0 | -0.0076129
j7 | t2 | 0 | 0 | 0 | -0.0076129
j7 | t3 | 0 | 0 | 0 | -0.0076129
j7 | t4 | 0 | 0 | 0 | -0.0076129
j7 | t5 | 0 | 0 | 0 | -0.0076129
j7 | t6 | 0 | 0 | 0 | -0.0076129
j7 | t7 | 0 | 0 | 0 | -0.0076129
j7 | t8 | 0 | -1.4211e-14 | 0 | -0.0076129
j7 | t9 | 0 | 0 | 0 | -0.011773
j7 | t10 | 0 | 0 | 0 | -0.011789
j7 | t11 | 0 | 0 | 0 | -0.011853
j7 | t12 | 0 | 0 | 0 | -0.011853
j7 | t13 | 0 | 0 | 0 | -0.011853
j7 | t14 | 0 | 0 | 0 | -0.011853
j7 | t15 | 0 | 0 | 0 | -0.011853
j7 | t16 | 0 | 0 | 0 | -0.011853
j7 | t17 | 0 | 0 | 0 | -0.011853
j7 | t18 | 0 | 0 | 0 | -0.011853
j7 | t19 | 0 | 0 | 0 | -0.011853
j7 | t20 | 0 | 0 | 0 | -0.011853
j7 | t21 | 0 | 0 | 0 | -0.011853
j7 | t22 | 0 | 3.5527e-15 | 0 | -0.011853
j7 | t23 | 0 | 0 | 0 | -0.011853
j7 | t24 | 0 | 0 | 0 | -0.011853
j10 | t1 | 0 | 0 | 0 | -0.0076129
j10 | t2 | 0 | 0 | 0 | -0.0076129
j10 | t3 | 0 | 0 | 0 | -0.0076129
j10 | t4 | 0 | 0 | 0 | -0.0076129
j10 | t5 | 0 | 0 | 0 | -0.0076129
j10 | t6 | 0 | 0 | 0 | -0.0076129
j10 | t7 | 0 | 0 | 0 | -0.0076129
j10 | t8 | 0 | 0 | 0 | -0.0076129
j10 | t9 | 0 | 0 | 0 | -0.011773
j10 | t10 | 0 | 0 | 0 | -0.011789
j10 | t11 | 0 | 0 | 0 | -0.011853
j10 | t12 | 0 | 0 | 0 | -0.011853
j10 | t13 | 0 | 0 | 0 | -0.011853
j10 | t14 | 0 | 0 | 0 | -0.011853
j10 | t15 | 0 | 0 | 0 | -0.011853
j10 | t16 | 0 | 0 | 0 | -0.011853
j10 | t17 | 0 | 0 | 0 | -0.011853
j10 | t18 | 0 | 0 | 0 | -0.011853
j10 | t19 | 0 | 0 | 0 | -0.011853
j10 | t20 | 0 | 0 | 0 | -0.011853
j10 | t21 | 0 | 0 | 0 | -0.011853
j10 | t22 | 0 | 0 | 0 | -0.011853
j10 | t23 | 0 | 0 | 0 | -0.011853
j10 | t24 | 0 | 0 | 0 | -0.011853

## Ordre_pompe
TOC
Ordre_pompe | (equation) | Les pompes s allument dans l ordre
c | d | t | Lowerbound | Value | Upperbound | Marginal
small | p1 | t1 | -INF | 0 | 0 | 0
small | p1 | t2 | -INF | 0 | 0 | 0
small | p1 | t3 | -INF | 0 | 0 | 0
small | p1 | t4 | -INF | 0 | 0 | 0
small | p1 | t5 | -INF | 0 | 0 | 0
small | p1 | t6 | -INF | 0 | 0 | 0
small | p1 | t7 | -INF | 0 | 0 | 0
small | p1 | t8 | -INF | 0 | 0 | 0
small | p1 | t9 | -INF | 0 | 0 | 0
small | p1 | t10 | -INF | 0 | 0 | 0
small | p1 | t11 | -INF | 0 | 0 | 0
small | p1 | t12 | -INF | 0 | 0 | 0
small | p1 | t13 | -INF | 0 | 0 | 0
small | p1 | t14 | -INF | 0 | 0 | 0
small | p1 | t15 | -INF | 0 | 0 | 0
small | p1 | t16 | -INF | 0 | 0 | 0
small | p1 | t17 | -INF | 0 | 0 | 0
small | p1 | t18 | -INF | 0 | 0 | 0
small | p1 | t19 | -INF | 0 | 0 | 0
small | p1 | t20 | -INF | 0 | 0 | 0
small | p1 | t21 | -INF | 0 | 0 | 0
small | p1 | t22 | -INF | 0 | 0 | 0
small | p1 | t23 | -INF | 0 | 0 | 0
small | p1 | t24 | -INF | 0 | 0 | 0
small | p2 | t1 | -INF | -1 | 0 | 0
small | p2 | t2 | -INF | -1 | 0 | 0
small | p2 | t3 | -INF | -1 | 0 | 0
small | p2 | t4 | -INF | -1 | 0 | 0
small | p2 | t5 | -INF | -1 | 0 | 0
small | p2 | t6 | -INF | -1 | 0 | 0
small | p2 | t7 | -INF | -1 | 0 | 0
small | p2 | t8 | -INF | -1 | 0 | 0
small | p2 | t9 | -INF | -1 | 0 | 0
small | p2 | t10 | -INF | -1 | 0 | 0
small | p2 | t11 | -INF | -1 | 0 | 0
small | p2 | t12 | -INF | -1 | 0 | 0
small | p2 | t13 | -INF | -1 | 0 | 0
small | p2 | t14 | -INF | -1 | 0 | 0
small | p2 | t15 | -INF | -1 | 0 | 0
small | p2 | t16 | -INF | -1 | 0 | 0
small | p2 | t17 | -INF | -1 | 0 | 0
small | p2 | t18 | -INF | -1 | 0 | 0
small | p2 | t19 | -INF | -1 | 0 | 0
small | p2 | t20 | -INF | -1 | 0 | 0
small | p2 | t21 | -INF | -1 | 0 | 0
small | p2 | t22 | -INF | -1 | 0 | 0
small | p2 | t23 | -INF | -1 | 0 | 0
small | p2 | t24 | -INF | -1 | 0 | 0
large | p1 | t1 | -INF | 0 | 0 | 0
large | p1 | t2 | -INF | 0 | 0 | 0
large | p1 | t3 | -INF | 0 | 0 | 0
large | p1 | t4 | -INF | 0 | 0 | 0
large | p1 | t5 | -INF | 0 | 0 | 0
large | p1 | t6 | -INF | 0 | 0 | 0
large | p1 | t7 | -INF | 0 | 0 | 0
large | p1 | t8 | -INF | 0 | 0 | 0
large | p1 | t9 | -INF | 0 | 0 | 0
large | p1 | t10 | -INF | 0 | 0 | 0
large | p1 | t11 | -INF | 0 | 0 | 0
large | p1 | t12 | -INF | 0 | 0 | 0
large | p1 | t13 | -INF | 0 | 0 | 0
large | p1 | t14 | -INF | 0 | 0 | 0
large | p1 | t15 | -INF | 0 | 0 | 0
large | p1 | t16 | -INF | 0 | 0 | 0
large | p1 | t17 | -INF | 0 | 0 | 0
large | p1 | t18 | -INF | 0 | 0 | 0
large | p1 | t19 | -INF | 0 | 0 | 0
large | p1 | t20 | -INF | 0 | 0 | 0
large | p1 | t21 | -INF | 0 | 0 | 0
large | p1 | t22 | -INF | 0 | 0 | 0
large | p1 | t23 | -INF | 0 | 0 | 0
large | p1 | t24 | -INF | 0 | 0 | 0
large | p2 | t1 | -INF | 0 | 0 | 0
large | p2 | t2 | -INF | 0 | 0 | 0
large | p2 | t3 | -INF | 0 | 0 | 0
large | p2 | t4 | -INF | 0 | 0 | 0
large | p2 | t5 | -INF | 0 | 0 | 0
large | p2 | t6 | -INF | 0 | 0 | 0
large | p2 | t7 | -INF | 0 | 0 | 0
large | p2 | t8 | -INF | 0 | 0 | 0
large | p2 | t9 | -INF | 0 | 0 | 0
large | p2 | t10 | -INF | 0 | 0 | 0
large | p2 | t11 | -INF | 0 | 0 | 0
large | p2 | t12 | -INF | 0 | 0 | 0
large | p2 | t13 | -INF | 0 | 0 | 0
large | p2 | t14 | -INF | 0 | 0 | 0
large | p2 | t15 | -INF | 0 | 0 | 0
large | p2 | t16 | -INF | 0 | 0 | 0
large | p2 | t17 | -INF | 0 | 0 | 0
large | p2 | t18 | -INF | 0 | 0 | 0
large | p2 | t19 | -INF | 0 | 0 | 0
large | p2 | t20 | -INF | 0 | 0 | 0
large | p2 | t21 | -INF | 0 | 0 | 0
large | p2 | t22 | -INF | 0 | 0 | 0
large | p2 | t23 | -INF | 0 | 0 | 0
large | p2 | t24 | -INF | 0 | 0 | 0
large | p3 | t1 | -INF | 0 | 0 | 0
large | p3 | t2 | -INF | 0 | 0 | 0
large | p3 | t3 | -INF | 0 | 0 | 0
large | p3 | t4 | -INF | 0 | 0 | 0
large | p3 | t5 | -INF | 0 | 0 | 0
large | p3 | t6 | -INF | 0 | 0 | 0
large | p3 | t7 | -INF | 0 | 0 | 0
large | p3 | t8 | -INF | 0 | 0 | 0
large | p3 | t9 | -INF | 0 | 0 | 0
large | p3 | t10 | -INF | 0 | 0 | 0
large | p3 | t11 | -INF | 0 | 0 | 0
large | p3 | t12 | -INF | 0 | 0 | 0
large | p3 | t13 | -INF | 0 | 0 | 0
large | p3 | t14 | -INF | 0 | 0 | 0
large | p3 | t15 | -INF | 0 | 0 | 0
large | p3 | t16 | -INF | 0 | 0 | 0
large | p3 | t17 | -INF | 0 | 0 | 0
large | p3 | t18 | -INF | 0 | 0 | 0
large | p3 | t19 | -INF | 0 | 0 | 0
large | p3 | t20 | -INF | 0 | 0 | 0
large | p3 | t21 | -INF | 0 | 0 | 0
large | p3 | t22 | -INF | 0 | 0 | 0
large | p3 | t23 | -INF | 0 | 0 | 0
large | p3 | t24 | -INF | 0 | 0 | 0
large | p4 | t1 | -INF | -1 | 0 | 0
large | p4 | t2 | -INF | -1 | 0 | 0
large | p4 | t3 | -INF | -1 | 0 | 0
large | p4 | t4 | -INF | -1 | 0 | 0
large | p4 | t5 | -INF | -1 | 0 | 0
large | p4 | t6 | -INF | -1 | 0 | 0
large | p4 | t7 | -INF | -1 | 0 | 0
large | p4 | t8 | -INF | -1 | 0 | 0
large | p4 | t9 | -INF | -1 | 0 | 0
large | p4 | t10 | -INF | -1 | 0 | 0
large | p4 | t11 | -INF | -1 | 0 | 0
large | p4 | t12 | -INF | -1 | 0 | 0
large | p4 | t13 | -INF | -1 | 0 | 0
large | p4 | t14 | -INF | -1 | 0 | 0
large | p4 | t15 | -INF | -1 | 0 | 0
large | p4 | t16 | -INF | -1 | 0 | 0
large | p4 | t17 | -INF | -1 | 0 | 0
large | p4 | t18 | -INF | -1 | 0 | 0
large | p4 | t19 | -INF | -1 | 0 | 0
large | p4 | t20 | -INF | -1 | 0 | 0
large | p4 | t21 | -INF | -1 | 0 | 0
large | p4 | t22 | -INF | -1 | 0 | 0
large | p4 | t23 | -INF | -1 | 0 | 0
large | p4 | t24 | -INF | -1 | 0 | 0

## Perte_charge
TOC
Perte_charge | (equation) | Perte charge (n n) Ã (t)
n | n | t | Lowerbound | Value | Upperbound | Marginal
s | j39 | t1 | 0 | 2.4425e-14 | 0 | 0.021677
s | j39 | t2 | 0 | 8.8818e-15 | 0 | 0.021654
s | j39 | t3 | 0 | 4.885e-15 | 0 | 0.021646
s | j39 | t4 | 0 | -1.6431e-14 | 0 | 0.021643
s | j39 | t5 | 0 | 0 | 0 | 0.021639
s | j39 | t6 | 0 | 2.2204e-14 | 0 | 0.021835
s | j39 | t7 | 0 | 1.4211e-14 | 0 | 0.022297
s | j39 | t8 | 0 | -3.3307e-14 | 0 | 0.023025
s | j39 | t9 | 0 | -1.1158e-14 | 0 | 0.0070735
s | j39 | t10 | 0 | 2.9754e-14 | 0 | 0.0079048
s | j39 | t11 | 0 | -9.3259e-15 | 0 | 0.016573
s | j39 | t12 | 0 | 3.9968e-15 | 0 | 0.016452
s | j39 | t13 | 0 | -1.5543e-14 | 0 | 0.01632
s | j39 | t14 | 0 | 1.0658e-14 | 0 | 0.016222
s | j39 | t15 | 0 | 1.9984e-14 | 0 | 0.016132
s | j39 | t16 | 0 | 6.4393e-15 | 0 | 0.016055
s | j39 | t17 | 0 | -1.1102e-15 | 0 | 0.015979
s | j39 | t18 | 0 | 1.1324e-14 | 0 | 0.015941
s | j39 | t19 | 0 | -5.107e-15 | 0 | 0.015874
s | j39 | t20 | 0 | 2.5313e-14 | 0 | 0.015828
s | j39 | t21 | 0 | 0 | 0 | 0.015782
s | j39 | t22 | 0 | 2.4425e-14 | 0 | 0.015866
s | j39 | t23 | 0 | -1.7764e-15 | 0 | 0.015842
s | j39 | t24 | 0 | 0 | 0 | 0.015804
j39 | j14 | t1 | 0 | -6.2172e-15 | 0 | 0.021677
j39 | j14 | t2 | 0 | 2.6645e-15 | 0 | 0.021654
j39 | j14 | t3 | 0 | 7.9936e-15 | 0 | 0.021646
j39 | j14 | t4 | 0 | 4.885e-15 | 0 | 0.021643
j39 | j14 | t5 | 0 | 9.77e-15 | 0 | 0.021639
j39 | j14 | t6 | 0 | -1.0658e-14 | 0 | 0.021835
j39 | j14 | t7 | 0 | -1.0214e-14 | 0 | 0.022297
j39 | j14 | t8 | 0 | -5.3291e-15 | 0 | 0.023025
j39 | j14 | t9 | 0 | -7.5495e-15 | 0 | 0.0070735
j39 | j14 | t10 | 0 | -1.5543e-15 | 0 | 0.0079048
j39 | j14 | t11 | 0 | -4.4409e-15 | 0 | 0.016573
j39 | j14 | t12 | 0 | 0 | 0 | 0.016452
j39 | j14 | t13 | 0 | 1.2434e-14 | 0 | 0.01632
j39 | j14 | t14 | 0 | 8.8818e-15 | 0 | 0.016222
j39 | j14 | t15 | 0 | -2.2204e-15 | 0 | 0.016132
j39 | j14 | t16 | 0 | 1.3323e-14 | 0 | 0.016055
j39 | j14 | t17 | 0 | -1.7764e-15 | 0 | 0.015979
j39 | j14 | t18 | 0 | 3.1086e-15 | 0 | 0.015941
j39 | j14 | t19 | 0 | -1.0658e-14 | 0 | 0.015874
j39 | j14 | t20 | 0 | 1.3323e-15 | 0 | 0.015828
j39 | j14 | t21 | 0 | -1.7319e-14 | 0 | 0.015782
j39 | j14 | t22 | 0 | -6.6613e-15 | 0 | 0.015866
j39 | j14 | t23 | 0 | 7.1054e-15 | 0 | 0.015842
j39 | j14 | t24 | 0 | -7.1054e-15 | 0 | 0.015804
j39 | j2 | t1 | 0 | 5.3291e-15 | 0 | 0
j39 | j2 | t2 | 0 | 9.77e-15 | 0 | 0
j39 | j2 | t3 | 0 | -1.7764e-14 | 0 | 0
j39 | j2 | t4 | 0 | 6.2172e-15 | 0 | 0
j39 | j2 | t5 | 0 | 1.5987e-14 | 0 | 0
j39 | j2 | t6 | 0 | 1.7764e-15 | 0 | 0
j39 | j2 | t7 | 0 | 1.6875e-14 | 0 | 0
j39 | j2 | t8 | 0 | 1.3323e-15 | 0 | 0
j39 | j2 | t9 | 0 | -1.3545e-14 | 0 | 0
j39 | j2 | t10 | 0 | -4.4409e-15 | 0 | 0
j39 | j2 | t11 | 0 | 3.1086e-15 | 0 | 0
j39 | j2 | t12 | 0 | -2.8866e-15 | 0 | 0
j39 | j2 | t13 | 0 | 1.2434e-14 | 0 | 0
j39 | j2 | t14 | 0 | 1.0436e-14 | 0 | 0
j39 | j2 | t15 | 0 | 5.9952e-15 | 0 | 0
j39 | j2 | t16 | 0 | 1.5543e-15 | 0 | 0
j39 | j2 | t17 | 0 | 0 | 0 | 0
j39 | j2 | t18 | 0 | -5.5511e-15 | 0 | 0
j39 | j2 | t19 | 0 | -1.3767e-14 | 0 | 0
j39 | j2 | t20 | 0 | 3.9968e-15 | 0 | 0
j39 | j2 | t21 | 0 | 1.1324e-14 | 0 | 0
j39 | j2 | t22 | 0 | 1.1102e-14 | 0 | 0
j39 | j2 | t23 | 0 | -1.2657e-14 | 0 | 0
j39 | j2 | t24 | 0 | 0 | 0 | 0
j14 | j16 | t1 | 0 | -1.2212e-14 | 0 | 0.021677
j14 | j16 | t2 | 0 | -1.199e-14 | 0 | 0.021654
j14 | j16 | t3 | 0 | -1.6653e-14 | 0 | 0.021646
j14 | j16 | t4 | 0 | -5.107e-15 | 0 | 0.021643
j14 | j16 | t5 | 0 | 2.8866e-15 | 0 | 0.021639
j14 | j16 | t6 | 0 | 2.2427e-14 | 0 | 0.021835
j14 | j16 | t7 | 0 | 5.7732e-15 | 0 | 0.022297
j14 | j16 | t8 | 0 | 8.6597e-15 | 0 | 0.023025
j14 | j16 | t9 | 0 | -3.2641e-14 | 0 | 0.0070735
j14 | j16 | t10 | 0 | -1.1768e-14 | 0 | 0.0079048
j14 | j16 | t11 | 0 | 4.6629e-15 | 0 | 0.016573
j14 | j16 | t12 | 0 | -1.5543e-14 | 0 | 0.016452
j14 | j16 | t13 | 0 | 4.2188e-15 | 0 | 0.01632
j14 | j16 | t14 | 0 | 0 | 0 | 0.016222
j14 | j16 | t15 | 0 | -9.77e-15 | 0 | 0.016132
j14 | j16 | t16 | 0 | 1.4211e-14 | 0 | 0.016055
j14 | j16 | t17 | 0 | -1.3323e-15 | 0 | 0.015979
j14 | j16 | t18 | 0 | 1.6431e-14 | 0 | 0.015941
j14 | j16 | t19 | 0 | 1.1102e-14 | 0 | 0.015874
j14 | j16 | t20 | 0 | -2.6645e-15 | 0 | 0.015828
j14 | j16 | t21 | 0 | -1.2434e-14 | 0 | 0.015782
j14 | j16 | t22 | 0 | -1.4655e-14 | 0 | 0.015866
j14 | j16 | t23 | 0 | 8.4377e-15 | 0 | 0.015842
j14 | j16 | t24 | 0 | -1.1546e-14 | 0 | 0.015804
j14 | r12 | t1 | 0 | -8.4377e-15 | 0 | 0
j14 | r12 | t2 | 0 | -4.4409e-15 | 0 | 0
j14 | r12 | t3 | 0 | 7.1054e-15 | 0 | 0
j14 | r12 | t4 | 0 | -7.1054e-15 | 0 | 0
j14 | r12 | t5 | 0 | -1.0214e-14 | 0 | 0
j14 | r12 | t6 | 0 | -1.2434e-14 | 0 | 0
j14 | r12 | t7 | 0 | 0 | 0 | 0
j14 | r12 | t8 | 0 | 2.2204e-15 | 0 | 0
j14 | r12 | t9 | 0 | 1.0159e-14 | 0 | 0
j14 | r12 | t10 | 0 | -1.8874e-15 | 0 | 0
j14 | r12 | t11 | 0 | 1.1324e-14 | 0 | 0
j14 | r12 | t12 | 0 | -1.1102e-15 | 0 | 0
j14 | r12 | t13 | 0 | -7.5495e-15 | 0 | 0
j14 | r12 | t14 | 0 | 4.4409e-15 | 0 | 0
j14 | r12 | t15 | 0 | -2.6645e-15 | 0 | 0
j14 | r12 | t16 | 0 | 1.2434e-14 | 0 | 0
j14 | r12 | t17 | 0 | -2.1316e-14 | 0 | 0
j14 | r12 | t18 | 0 | 1.5543e-15 | 0 | 0
j14 | r12 | t19 | 0 | -5.7732e-15 | 0 | 0
j14 | r12 | t20 | 0 | -1.1546e-14 | 0 | 0
j14 | r12 | t21 | 0 | 1.2212e-14 | 0 | 0
j14 | r12 | t22 | 0 | 0 | 0 | 0
j14 | r12 | t23 | 0 | 2.8866e-15 | 0 | 0
j14 | r12 | t24 | 0 | 1.2434e-14 | 0 | 0
j16 | j17 | t1 | 0 | -5.9952e-15 | 0 | 0.021677
j16 | j17 | t2 | 0 | 1.8874e-14 | 0 | 0.021654
j16 | j17 | t3 | 0 | 4.4409e-15 | 0 | 0.021646
j16 | j17 | t4 | 0 | 1.199e-14 | 0 | 0.021643
j16 | j17 | t5 | 0 | -2.8866e-15 | 0 | 0.021639
j16 | j17 | t6 | 0 | -7.7716e-15 | 0 | 0.021835
j16 | j17 | t7 | 0 | -4.885e-15 | 0 | 0.022297
j16 | j17 | t8 | 0 | 7.3275e-15 | 0 | 0.023025
j16 | j17 | t9 | 0 | 6.9944e-15 | 0 | 0.0070735
j16 | j17 | t10 | 0 | 2.4092e-14 | 0 | 0.0079048
j16 | j17 | t11 | 0 | 0 | 0 | 0.016573
j16 | j17 | t12 | 0 | 7.5495e-15 | 0 | 0.016452
j16 | j17 | t13 | 0 | -1.199e-14 | 0 | 0.01632
j16 | j17 | t14 | 0 | -1.2434e-14 | 0 | 0.016222
j16 | j17 | t15 | 0 | -1.7097e-14 | 0 | 0.016132
j16 | j17 | t16 | 0 | 3.7748e-15 | 0 | 0.016055
j16 | j17 | t17 | 0 | 8.4377e-15 | 0 | 0.015979
j16 | j17 | t18 | 0 | -5.7732e-15 | 0 | 0.015941
j16 | j17 | t19 | 0 | -1.0214e-14 | 0 | 0.015874
j16 | j17 | t20 | 0 | -1.5543e-14 | 0 | 0.015828
j16 | j17 | t21 | 0 | 2.1538e-14 | 0 | 0.015782
j16 | j17 | t22 | 0 | -6.6613e-15 | 0 | 0.015866
j16 | j17 | t23 | 0 | 7.7716e-15 | 0 | 0.015842
j16 | j17 | t24 | 0 | -1.5765e-14 | 0 | 0.015804
j16 | j24 | t1 | 0 | 7.3223e-15 | 0 | 0
j16 | j24 | t2 | 0 | 1.7516e-14 | 0 | 0
j16 | j24 | t3 | 0 | 1.2157e-14 | 0 | 0
j16 | j24 | t4 | 0 | 9.2305e-15 | 0 | 0
j16 | j24 | t5 | 0 | -9.9382e-15 | 0 | 0
j16 | j24 | t6 | 0 | 1.1812e-14 | 0 | 0
j16 | j24 | t7 | 0 | 1.0247e-14 | 0 | 0
j16 | j24 | t8 | 0 | 7.9554e-15 | 0 | 0
j16 | j24 | t9 | 0 | 0 | 0 | 0
j16 | j24 | t10 | 0 | 0 | 0 | 0
j16 | j24 | t11 | 0 | -1.1588e-14 | 0 | 0
j16 | j24 | t12 | 0 | -1.2584e-14 | 0 | 0
j16 | j24 | t13 | 0 | -9.6e-15 | 0 | 0
j16 | j24 | t14 | 0 | 1.1047e-14 | 0 | 0
j16 | j24 | t15 | 0 | 4.1807e-15 | 0 | 0
j16 | j24 | t16 | 0 | -1.0186e-14 | 0 | 0
j16 | j24 | t17 | 0 | -1.7937e-15 | 0 | 0
j16 | j24 | t18 | 0 | 8.0665e-15 | 0 | 0
j16 | j24 | t19 | 0 | 8.3752e-15 | 0 | 0
j16 | j24 | t20 | 0 | 1.8804e-15 | 0 | 0
j16 | j24 | t21 | 0 | -1.1244e-14 | 0 | 0
j16 | j24 | t22 | 0 | -1.318e-14 | 0 | 0
j16 | j24 | t23 | 0 | -9.0448e-15 | 0 | 0
j16 | j24 | t24 | 0 | -9.0657e-15 | 0 | 0
j17 | j19 | t1 | 0 | 7.9936e-15 | 0 | 0.021677
j17 | j19 | t2 | 0 | -2.1316e-14 | 0 | 0.021654
j17 | j19 | t3 | 0 | -7.1054e-15 | 0 | 0.021646
j17 | j19 | t4 | 0 | 2.1316e-14 | 0 | 0.021643
j17 | j19 | t5 | 0 | 1.5987e-14 | 0 | 0.021639
j17 | j19 | t6 | 0 | 1.5099e-14 | 0 | 0.021835
j17 | j19 | t7 | 0 | 1.3323e-14 | 0 | 0.022297
j17 | j19 | t8 | 0 | -3.1086e-15 | 0 | 0.023025
j17 | j19 | t9 | 0 | -5.3291e-15 | 0 | 0.0070735
j17 | j19 | t10 | 0 | -1.8652e-14 | 0 | 0.0079048
j17 | j19 | t11 | 0 | -6.6613e-15 | 0 | 0.016573
j17 | j19 | t12 | 0 | -4.4409e-15 | 0 | 0.016452
j17 | j19 | t13 | 0 | -2.2204e-15 | 0 | 0.01632
j17 | j19 | t14 | 0 | 1.3323e-14 | 0 | 0.016222
j17 | j19 | t15 | 0 | -7.5495e-15 | 0 | 0.016132
j17 | j19 | t16 | 0 | -4.885e-15 | 0 | 0.016055
j17 | j19 | t17 | 0 | -4.885e-15 | 0 | 0.015979
j17 | j19 | t18 | 0 | 1.7764e-14 | 0 | 0.015941
j17 | j19 | t19 | 0 | -3.5527e-15 | 0 | 0.015874
j17 | j19 | t20 | 0 | -8.8818e-15 | 0 | 0.015828
j17 | j19 | t21 | 0 | -2.4425e-14 | 0 | 0.015782
j17 | j19 | t22 | 0 | 3.1086e-15 | 0 | 0.015866
j17 | j19 | t23 | 0 | 6.6613e-15 | 0 | 0.015842
j17 | j19 | t24 | 0 | 1.0214e-14 | 0 | 0.015804
j17 | r13 | t1 | 0 | -4.4409e-15 | 0 | 0
j17 | r13 | t2 | 0 | -1.2434e-14 | 0 | 0
j17 | r13 | t3 | 0 | -1.1546e-14 | 0 | 0
j17 | r13 | t4 | 0 | 7.9936e-15 | 0 | 0
j17 | r13 | t5 | 0 | 2.6645e-15 | 0 | 0
j17 | r13 | t6 | 0 | 1.4211e-14 | 0 | 0
j17 | r13 | t7 | 0 | 1.8652e-14 | 0 | 0
j17 | r13 | t8 | 0 | 0 | 0 | 0
j17 | r13 | t9 | 0 | 0 | 0 | 0
j17 | r13 | t10 | 0 | 0 | 0 | 0
j17 | r13 | t11 | 0 | 0 | 0 | 0
j17 | r13 | t12 | 0 | 0 | 0 | 0
j17 | r13 | t13 | 0 | 0 | 0 | 0
j17 | r13 | t14 | 0 | 0 | 0 | 0
j17 | r13 | t15 | 0 | 0 | 0 | 0
j17 | r13 | t16 | 0 | 0 | 0 | 0
j17 | r13 | t17 | 0 | 0 | 0 | 0
j17 | r13 | t18 | 0 | 0 | 0 | 0
j17 | r13 | t19 | 0 | 0 | 0 | 0
j17 | r13 | t20 | 0 | 0 | 0 | 0
j17 | r13 | t21 | 0 | 0 | 0 | 0
j17 | r13 | t22 | 0 | 0 | 0 | 0
j17 | r13 | t23 | 0 | 0 | 0 | 0
j17 | r13 | t24 | 0 | 0 | 0 | 0
j19 | j21 | t1 | 0 | 2.2649e-14 | 0 | 0.021677
j19 | j21 | t2 | 0 | 3.1086e-14 | 0 | 0.021654
j19 | j21 | t3 | 0 | 0 | 0 | 0.021646
j19 | j21 | t4 | 0 | 1.2434e-14 | 0 | 0.021643
j19 | j21 | t5 | 0 | -3.1086e-15 | 0 | 0.021639
j19 | j21 | t6 | 0 | -1.1102e-14 | 0 | 0.021835
j19 | j21 | t7 | 0 | -9.77e-15 | 0 | 0.022297
j19 | j21 | t8 | 0 | 4.885e-15 | 0 | 0.023025
j19 | j21 | t9 | 0 | -3.9968e-15 | 0 | 0.0070735
j19 | j21 | t10 | 0 | 8.8818e-15 | 0 | 0.0079048
j19 | j21 | t11 | 0 | 2.3537e-14 | 0 | 0.016573
j19 | j21 | t12 | 0 | -2.6645e-15 | 0 | 0.016452
j19 | j21 | t13 | 0 | -2.6645e-15 | 0 | 0.01632
j19 | j21 | t14 | 0 | -1.6875e-14 | 0 | 0.016222
j19 | j21 | t15 | 0 | -2.5757e-14 | 0 | 0.016132
j19 | j21 | t16 | 0 | -1.954e-14 | 0 | 0.016055
j19 | j21 | t17 | 0 | -1.7319e-14 | 0 | 0.015979
j19 | j21 | t18 | 0 | -3.9968e-15 | 0 | 0.015941
j19 | j21 | t19 | 0 | 1.9096e-14 | 0 | 0.015874
j19 | j21 | t20 | 0 | 0 | 0 | 0.015828
j19 | j21 | t21 | 0 | 1.2434e-14 | 0 | 0.015782
j19 | j21 | t22 | 0 | -3.9968e-15 | 0 | 0.015866
j19 | j21 | t23 | 0 | 5.7732e-15 | 0 | 0.015842
j19 | j21 | t24 | 0 | 1.4211e-14 | 0 | 0.015804
j19 | r132 | t1 | 0 | 1.088e-14 | 0 | 0
j19 | r132 | t2 | 0 | 1.0769e-14 | 0 | 0
j19 | r132 | t3 | 0 | -1.088e-14 | 0 | 0
j19 | r132 | t4 | 0 | 0 | 0 | 0
j19 | r132 | t5 | 0 | -9.992e-15 | 0 | 0
j19 | r132 | t6 | 0 | 8.3267e-15 | 0 | 0
j19 | r132 | t7 | 0 | -4.1078e-15 | 0 | 0
j19 | r132 | t8 | 0 | -1.1324e-14 | 0 | 0
j19 | r132 | t9 | 0 | -1.3295e-14 | 0 | 0
j19 | r132 | t10 | 0 | -1.0991e-14 | 0 | 0
j19 | r132 | t11 | 0 | 6.3283e-15 | 0 | 0
j19 | r132 | t12 | 0 | -6.1617e-15 | 0 | 0
j19 | r132 | t13 | 0 | -6.7724e-15 | 0 | 0
j19 | r132 | t14 | 0 | -1.3323e-14 | 0 | 0
j19 | r132 | t15 | 0 | 2.6645e-15 | 0 | 0
j19 | r132 | t16 | 0 | 1.3489e-14 | 0 | 0
j19 | r132 | t17 | 0 | 7.6605e-15 | 0 | 0
j19 | r132 | t18 | 0 | 1.1047e-14 | 0 | 0
j19 | r132 | t19 | 0 | 1.4155e-14 | 0 | 0
j19 | r132 | t20 | 0 | -1.0825e-14 | 0 | 0
j19 | r132 | t21 | 0 | 1.0159e-14 | 0 | 0
j19 | r132 | t22 | 0 | 0 | 0 | 0
j19 | r132 | t23 | 0 | -1.1491e-14 | 0 | 0
j19 | r132 | t24 | 0 | 1.1102e-15 | 0 | 0
j21 | r133 | t1 | 0 | -4.1078e-15 | 0 | 0
j21 | r133 | t2 | 0 | 8.6597e-15 | 0 | 0
j21 | r133 | t3 | 0 | -1.1324e-14 | 0 | 0
j21 | r133 | t4 | 0 | -1.2323e-14 | 0 | 0
j21 | r133 | t5 | 0 | 5.7732e-15 | 0 | 0
j21 | r133 | t6 | 0 | 1.1102e-14 | 0 | 0
j21 | r133 | t7 | 0 | -3.7748e-15 | 0 | 0
j21 | r133 | t8 | 0 | -9.3259e-15 | 0 | 0
j21 | r133 | t9 | 0 | 1.1879e-14 | 0 | 0
j21 | r133 | t10 | 0 | 1.2712e-14 | 0 | 0
j21 | r133 | t11 | 0 | -8.1046e-15 | 0 | 0
j21 | r133 | t12 | 0 | 3.6637e-15 | 0 | 0
j21 | r133 | t13 | 0 | 1.3323e-15 | 0 | 0
j21 | r133 | t14 | 0 | -9.5479e-15 | 0 | 0
j21 | r133 | t15 | 0 | -9.77e-15 | 0 | 0
j21 | r133 | t16 | 0 | -1.3323e-15 | 0 | 0
j21 | r133 | t17 | 0 | 1.2434e-14 | 0 | 0
j21 | r133 | t18 | 0 | 1.3989e-14 | 0 | 0
j21 | r133 | t19 | 0 | 1.3989e-14 | 0 | 0
j21 | r133 | t20 | 0 | 3.5527e-15 | 0 | 0
j21 | r133 | t21 | 0 | -4.1078e-15 | 0 | 0
j21 | r133 | t22 | 0 | 2.9976e-15 | 0 | 0
j21 | r133 | t23 | 0 | 5.3291e-15 | 0 | 0
j21 | r133 | t24 | 0 | -9.992e-15 | 0 | 0
j21 | r134 | t1 | 0 | 8.9789e-15 | 0 | 0.021677
j21 | r134 | t2 | 0 | 4.7462e-15 | 0 | 0.021654
j21 | r134 | t3 | 0 | 9.5028e-15 | 0 | 0.021646
j21 | r134 | t4 | 0 | -9.2253e-15 | 0 | 0.021643
j21 | r134 | t5 | 0 | 1.3402e-14 | 0 | 0.021639
j21 | r134 | t6 | 0 | 1.2407e-14 | 0 | 0.021835
j21 | r134 | t7 | 0 | 0 | 0 | 0.022297
j21 | r134 | t8 | 0 | 9.6589e-15 | 0 | 0.023025
j21 | r134 | t9 | 0 | -4.1078e-15 | 0 | 0.0070735
j21 | r134 | t10 | 0 | 8.7985e-15 | 0 | 0.0079048
j21 | r134 | t11 | 0 | 0 | 0 | 0.016573
j21 | r134 | t12 | 0 | 0 | 0 | 0.016452
j21 | r134 | t13 | 0 | 0 | 0 | 0.01632
j21 | r134 | t14 | 0 | 0 | 0 | 0.016222
j21 | r134 | t15 | 0 | 0 | 0 | 0.016132
j21 | r134 | t16 | 0 | 0 | 0 | 0.016055
j21 | r134 | t17 | 0 | 0 | 0 | 0.015979
j21 | r134 | t18 | 0 | 0 | 0 | 0.015941
j21 | r134 | t19 | 0 | 0 | 0 | 0.015874
j21 | r134 | t20 | 0 | 0 | 0 | 0.015828
j21 | r134 | t21 | 0 | -1.1748e-14 | 0 | 0.015782
j21 | r134 | t22 | 0 | -5.9952e-15 | 0 | 0.015866
j21 | r134 | t23 | 0 | 9.1593e-15 | 0 | 0.015842
j21 | r134 | t24 | 0 | 0 | 0 | 0.015804
j24 | j26 | t1 | 0 | 5.3291e-15 | 0 | 0
j24 | j26 | t2 | 0 | 2.6645e-15 | 0 | 0
j24 | j26 | t3 | 0 | 1.7764e-15 | 0 | 0
j24 | j26 | t4 | 0 | 1.3323e-14 | 0 | 0
j24 | j26 | t5 | 0 | 1.2434e-14 | 0 | 0
j24 | j26 | t6 | 0 | -4.4409e-15 | 0 | 0
j24 | j26 | t7 | 0 | 6.2172e-15 | 0 | 0
j24 | j26 | t8 | 0 | -7.9936e-15 | 0 | 0
j24 | j26 | t9 | 0 | -3.9968e-15 | 0 | 0
j24 | j26 | t10 | 0 | -9.77e-15 | 0 | 0
j24 | j26 | t11 | 0 | -1.3323e-14 | 0 | 0
j24 | j26 | t12 | 0 | 1.4211e-14 | 0 | 0
j24 | j26 | t13 | 0 | 2.3981e-14 | 0 | 0
j24 | j26 | t14 | 0 | -1.7764e-14 | 0 | 0
j24 | j26 | t15 | 0 | -1.7764e-15 | 0 | 0
j24 | j26 | t16 | 0 | -2.2204e-14 | 0 | 0
j24 | j26 | t17 | 0 | 2.6645e-15 | 0 | 0
j24 | j26 | t18 | 0 | -5.3291e-15 | 0 | 0
j24 | j26 | t19 | 0 | 7.9936e-15 | 0 | 0
j24 | j26 | t20 | 0 | -1.5987e-14 | 0 | 0
j24 | j26 | t21 | 0 | 0 | 0 | 0
j24 | j26 | t22 | 0 | -1.2434e-14 | 0 | 0
j24 | j26 | t23 | 0 | 1.7764e-15 | 0 | 0
j24 | j26 | t24 | 0 | 5.3291e-15 | 0 | 0
j24 | r14 | t1 | 0 | 2.2447e-15 | 0 | 0
j24 | r14 | t2 | 0 | 0 | 0 | 0
j24 | r14 | t3 | 0 | 0 | 0 | 0
j24 | r14 | t4 | 0 | 0 | 0 | 0
j24 | r14 | t5 | 0 | -1.138e-14 | 0 | 0
j24 | r14 | t6 | 0 | -4.3299e-15 | 0 | 0
j24 | r14 | t7 | 0 | 0 | 0 | 0
j24 | r14 | t8 | 0 | -1.0103e-14 | 0 | 0
j24 | r14 | t9 | 0 | 0 | 0 | 0
j24 | r14 | t10 | 0 | 7.3188e-15 | 0 | 0
j24 | r14 | t11 | 0 | 0 | 0 | 0
j24 | r14 | t12 | 0 | 0 | 0 | 0
j24 | r14 | t13 | 0 | 0 | 0 | 0
j24 | r14 | t14 | 0 | 0 | 0 | 0
j24 | r14 | t15 | 0 | 8.4932e-15 | 0 | 0
j24 | r14 | t16 | 0 | 0 | 0 | 0
j24 | r14 | t17 | 0 | 0 | 0 | 0
j24 | r14 | t18 | 0 | 0 | 0 | 0
j24 | r14 | t19 | 0 | 0 | 0 | 0
j24 | r14 | t20 | 0 | 0 | 0 | 0
j24 | r14 | t21 | 0 | 0 | 0 | 0
j24 | r14 | t22 | 0 | 0 | 0 | 0
j24 | r14 | t23 | 0 | 0 | 0 | 0
j24 | r14 | t24 | 0 | -1.3605e-14 | 0 | 0
j26 | j27 | t1 | 0 | -1.6098e-15 | 0 | 0
j26 | j27 | t2 | 0 | 1.3323e-14 | 0 | 0
j26 | j27 | t3 | 0 | -7.9936e-15 | 0 | 0
j26 | j27 | t4 | 0 | 0 | 0 | 0
j26 | j27 | t5 | 0 | 1.0013e-14 | 0 | 0
j26 | j27 | t6 | 0 | 0 | 0 | 0
j26 | j27 | t7 | 0 | -7.5495e-15 | 0 | 0
j26 | j27 | t8 | 0 | -1.2365e-14 | 0 | 0
j26 | j27 | t9 | 0 | 5.1747e-15 | 0 | 0
j26 | j27 | t10 | 0 | -8.9373e-15 | 0 | 0
j26 | j27 | t11 | 0 | 2.7756e-15 | 0 | 0
j26 | j27 | t12 | 0 | 0 | 0 | 0
j26 | j27 | t13 | 0 | 1.8208e-14 | 0 | 0
j26 | j27 | t14 | 0 | 3.4861e-14 | 0 | 0
j26 | j27 | t15 | 0 | -1.5099e-14 | 0 | 0
j26 | j27 | t16 | 0 | 5.509e-15 | 0 | 0
j26 | j27 | t17 | 0 | -1.7764e-15 | 0 | 0
j26 | j27 | t18 | 0 | 8.8055e-15 | 0 | 0
j26 | j27 | t19 | 0 | 0 | 0 | 0
j26 | j27 | t20 | 0 | 0 | 0 | 0
j26 | j27 | t21 | 0 | 9.2704e-15 | 0 | 0
j26 | j27 | t22 | 0 | -5.9952e-15 | 0 | 0
j26 | j27 | t23 | 0 | 5.7732e-15 | 0 | 0
j26 | j27 | t24 | 0 | -6.1062e-15 | 0 | 0
j26 | j30 | t1 | 0 | 6.6613e-15 | 0 | 0
j26 | j30 | t2 | 0 | 2.8866e-15 | 0 | 0
j26 | j30 | t3 | 0 | 6.6891e-15 | 0 | 0
j26 | j30 | t4 | 0 | -1.7764e-15 | 0 | 0
j26 | j30 | t5 | 0 | 5.3291e-15 | 0 | 0
j26 | j30 | t6 | 0 | -1.3323e-14 | 0 | 0
j26 | j30 | t7 | 0 | 0 | 0 | 0
j26 | j30 | t8 | 0 | -1.5543e-14 | 0 | 0
j26 | j30 | t9 | 0 | 0 | 0 | 0
j26 | j30 | t10 | 0 | 1.0769e-14 | 0 | 0
j26 | j30 | t11 | 0 | -3.9968e-15 | 0 | 0
j26 | j30 | t12 | 0 | 0 | 0 | 0
j26 | j30 | t13 | 0 | 0 | 0 | 0
j26 | j30 | t14 | 0 | -3.9968e-15 | 0 | 0
j26 | j30 | t15 | 0 | -1.1102e-14 | 0 | 0
j26 | j30 | t16 | 0 | 4.2633e-14 | 0 | 0
j26 | j30 | t17 | 0 | 0 | 0 | 0
j26 | j30 | t18 | 0 | 1.7764e-14 | 0 | 0
j26 | j30 | t19 | 0 | 3.5527e-15 | 0 | 0
j26 | j30 | t20 | 0 | 0 | 0 | 0
j26 | j30 | t21 | 0 | 2.5757e-14 | 0 | 0
j26 | j30 | t22 | 0 | 1.1102e-14 | 0 | 0
j26 | j30 | t23 | 0 | -1.1102e-14 | 0 | 0
j26 | j30 | t24 | 0 | 3.1086e-15 | 0 | 0
j27 | r16 | t1 | 0 | 7.2407e-15 | 0 | 0
j27 | r16 | t2 | 0 | 2.7875e-15 | 0 | 0
j27 | r16 | t3 | 0 | -1.0326e-14 | 0 | 0
j27 | r16 | t4 | 0 | 0 | 0 | 0
j27 | r16 | t5 | 0 | 1.0315e-14 | 0 | 0
j27 | r16 | t6 | 0 | 0 | 0 | 0
j27 | r16 | t7 | 0 | 7.435e-15 | 0 | 0
j27 | r16 | t8 | 0 | -6.0292e-15 | 0 | 0
j27 | r16 | t9 | 0 | -1.1789e-14 | 0 | 0
j27 | r16 | t10 | 0 | -2.2846e-15 | 0 | 0
j27 | r16 | t11 | 0 | -4.1713e-15 | 0 | 0
j27 | r16 | t12 | 0 | 0 | 0 | 0
j27 | r16 | t13 | 0 | -2.8276e-15 | 0 | 0
j27 | r16 | t14 | 0 | 0 | 0 | 0
j27 | r16 | t15 | 0 | 0 | 0 | 0
j27 | r16 | t16 | 0 | 0 | 0 | 0
j27 | r16 | t17 | 0 | 1.0945e-14 | 0 | 0
j27 | r16 | t18 | 0 | 2.6693e-15 | 0 | 0
j27 | r16 | t19 | 0 | 0 | 0 | 0
j27 | r16 | t20 | 0 | 1.0152e-14 | 0 | 0
j27 | r16 | t21 | 0 | 0 | 0 | 0
j27 | r16 | t22 | 0 | 0 | 0 | 0
j27 | r16 | t23 | 0 | -1.0164e-14 | 0 | 0
j27 | r16 | t24 | 0 | 8.3241e-15 | 0 | 0
j27 | r161 | t1 | 0 | 2.6645e-15 | 0 | 0
j27 | r161 | t2 | 0 | -3.5527e-15 | 0 | 0
j27 | r161 | t3 | 0 | 1.4211e-14 | 0 | 0
j27 | r161 | t4 | 0 | 0 | 0 | 0
j27 | r161 | t5 | 0 | -9.809e-15 | 0 | 0
j27 | r161 | t6 | 0 | 0 | 0 | 0
j27 | r161 | t7 | 0 | 3.1974e-14 | 0 | 0
j27 | r161 | t8 | 0 | 1.7764e-14 | 0 | 0
j27 | r161 | t9 | 0 | 1.1935e-14 | 0 | 0
j27 | r161 | t10 | 0 | 0 | 0 | 0
j27 | r161 | t11 | 0 | 0 | 0 | 0
j27 | r161 | t12 | 0 | 0 | 0 | 0
j27 | r161 | t13 | 0 | -1.4211e-14 | 0 | 0
j27 | r161 | t14 | 0 | -1.7764e-14 | 0 | 0
j27 | r161 | t15 | 0 | -2.931e-14 | 0 | 0
j27 | r161 | t16 | 0 | 1.1567e-14 | 0 | 0
j27 | r161 | t17 | 0 | -3.5527e-14 | 0 | 0
j27 | r161 | t18 | 0 | 0 | 0 | 0
j27 | r161 | t19 | 0 | 0 | 0 | 0
j27 | r161 | t20 | 0 | 3.5527e-15 | 0 | 0
j27 | r161 | t21 | 0 | -9.2704e-15 | 0 | 0
j27 | r161 | t22 | 0 | -1.7764e-14 | 0 | 0
j27 | r161 | t23 | 0 | 5.3291e-15 | 0 | 0
j27 | r161 | t24 | 0 | 4.4409e-15 | 0 | 0
j30 | r15 | t1 | 0 | 8.5487e-15 | 0 | 0
j30 | r15 | t2 | 0 | 3.0531e-15 | 0 | 0
j30 | r15 | t3 | 0 | 0 | 0 | 0
j30 | r15 | t4 | 0 | 0 | 0 | 0
j30 | r15 | t5 | 0 | -1.7764e-15 | 0 | 0
j30 | r15 | t6 | 0 | -6.7637e-15 | 0 | 0
j30 | r15 | t7 | 0 | 0 | 0 | 0
j30 | r15 | t8 | 0 | -8.6042e-15 | 0 | 0
j30 | r15 | t9 | 0 | 5.9536e-15 | 0 | 0
j30 | r15 | t10 | 0 | -8.8679e-15 | 0 | 0
j30 | r15 | t11 | 0 | -6.0438e-15 | 0 | 0
j30 | r15 | t12 | 0 | 6.1062e-15 | 0 | 0
j30 | r15 | t13 | 0 | 0 | 0 | 0
j30 | r15 | t14 | 0 | -3.9968e-15 | 0 | 0
j30 | r15 | t15 | 0 | -1.3323e-15 | 0 | 0
j30 | r15 | t16 | 0 | 0 | 0 | 0
j30 | r15 | t17 | 0 | 0 | 0 | 0
j30 | r15 | t18 | 0 | 5.7732e-15 | 0 | 0
j30 | r15 | t19 | 0 | 0 | 0 | 0
j30 | r15 | t20 | 0 | 0 | 0 | 0
j30 | r15 | t21 | 0 | 0 | 0 | 0
j30 | r15 | t22 | 0 | 0 | 0 | 0
j30 | r15 | t23 | 0 | 0 | 0 | 0
j30 | r15 | t24 | 0 | -1.3323e-15 | 0 | 0
j30 | r151 | t1 | 0 | -7.1054e-15 | 0 | 0
j30 | r151 | t2 | 0 | -1.4197e-14 | 0 | 0
j30 | r151 | t3 | 0 | -1.3753e-14 | 0 | 0
j30 | r151 | t4 | 0 | 2.4869e-14 | 0 | 0
j30 | r151 | t5 | 0 | 0 | 0 | 0
j30 | r151 | t6 | 0 | 1.0658e-14 | 0 | 0
j30 | r151 | t7 | 0 | 0 | 0 | 0
j30 | r151 | t8 | 0 | 3.5527e-15 | 0 | 0
j30 | r151 | t9 | 0 | 1.4377e-14 | 0 | 0
j30 | r151 | t10 | 0 | 1.5543e-15 | 0 | 0
j30 | r151 | t11 | 0 | 0 | 0 | 0
j30 | r151 | t12 | 0 | 1.7764e-15 | 0 | 0
j30 | r151 | t13 | 0 | 0 | 0 | 0
j30 | r151 | t14 | 0 | 1.2268e-14 | 0 | 0
j30 | r151 | t15 | 0 | -1.2879e-14 | 0 | 0
j30 | r151 | t16 | 0 | 3.1974e-14 | 0 | 0
j30 | r151 | t17 | 0 | 0 | 0 | 0
j30 | r151 | t18 | 0 | -1.1546e-14 | 0 | 0
j30 | r151 | t19 | 0 | 3.5527e-15 | 0 | 0
j30 | r151 | t20 | 0 | 0 | 0 | 0
j30 | r151 | t21 | 0 | -1.8874e-14 | 0 | 0
j30 | r151 | t22 | 0 | 5.3291e-15 | 0 | 0
j30 | r151 | t23 | 0 | 0 | 0 | 0
j30 | r151 | t24 | 0 | -6.2172e-15 | 0 | 0
j2 | j3 | t1 | 0 | -3.9968e-14 | 0 | 0
j2 | j3 | t2 | 0 | -1.8652e-14 | 0 | 0
j2 | j3 | t3 | 0 | 2.8422e-14 | 0 | 0
j2 | j3 | t4 | 0 | -8.8818e-15 | 0 | 0
j2 | j3 | t5 | 0 | 0 | 0 | 0
j2 | j3 | t6 | 0 | -1.5255e-15 | 0 | 0
j2 | j3 | t7 | 0 | 1.7764e-15 | 0 | 0
j2 | j3 | t8 | 0 | 3.5527e-15 | 0 | 0
j2 | j3 | t9 | 0 | -2.7756e-15 | 0 | 0
j2 | j3 | t10 | 0 | 0 | 0 | 0
j2 | j3 | t11 | 0 | 3.5527e-15 | 0 | 0
j2 | j3 | t12 | 0 | -5.3291e-15 | 0 | 0
j2 | j3 | t13 | 0 | 0 | 0 | 0
j2 | j3 | t14 | 0 | -1.3767e-14 | 0 | 0
j2 | j3 | t15 | 0 | 0 | 0 | 0
j2 | j3 | t16 | 0 | 0 | 0 | 0
j2 | j3 | t17 | 0 | 3.5527e-15 | 0 | 0
j2 | j3 | t18 | 0 | 0 | 0 | 0
j2 | j3 | t19 | 0 | 8.5973e-15 | 0 | 0
j2 | j3 | t20 | 0 | 0 | 0 | 0
j2 | j3 | t21 | 0 | -1.4211e-14 | 0 | 0
j2 | j3 | t22 | 0 | 0 | 0 | 0
j2 | j3 | t23 | 0 | 0 | 0 | 0
j2 | j3 | t24 | 0 | -2.6645e-15 | 0 | 0
j2 | j6 | t1 | 0 | -3.5527e-15 | 0 | 0
j2 | j6 | t2 | 0 | -1.7764e-14 | 0 | 0
j2 | j6 | t3 | 0 | 3.5527e-15 | 0 | 0
j2 | j6 | t4 | 0 | 1.4211e-14 | 0 | 0
j2 | j6 | t5 | 0 | 2.3093e-14 | 0 | 0
j2 | j6 | t6 | 0 | 1.7764e-14 | 0 | 0
j2 | j6 | t7 | 0 | -1.0658e-14 | 0 | 0
j2 | j6 | t8 | 0 | -1.5987e-14 | 0 | 0
j2 | j6 | t9 | 0 | -1.1102e-15 | 0 | 0
j2 | j6 | t10 | 0 | 5.3291e-15 | 0 | 0
j2 | j6 | t11 | 0 | -1.0658e-14 | 0 | 0
j2 | j6 | t12 | 0 | -2.8866e-15 | 0 | 0
j2 | j6 | t13 | 0 | 3.1974e-14 | 0 | 0
j2 | j6 | t14 | 0 | -8.8818e-15 | 0 | 0
j2 | j6 | t15 | 0 | 9.77e-15 | 0 | 0
j2 | j6 | t16 | 0 | 2.8422e-14 | 0 | 0
j2 | j6 | t17 | 0 | 7.1609e-15 | 0 | 0
j2 | j6 | t18 | 0 | 1.8652e-14 | 0 | 0
j2 | j6 | t19 | 0 | -1.1546e-14 | 0 | 0
j2 | j6 | t20 | 0 | 7.1054e-15 | 0 | 0
j2 | j6 | t21 | 0 | -1.0658e-14 | 0 | 0
j2 | j6 | t22 | 0 | -4.4409e-15 | 0 | 0
j2 | j6 | t23 | 0 | -4.4409e-15 | 0 | 0
j2 | j6 | t24 | 0 | 1.0214e-14 | 0 | 0
j3 | r17 | t1 | 0 | -1.0075e-14 | 0 | 0
j3 | r17 | t2 | 0 | 0 | 0 | 0
j3 | r17 | t3 | 0 | -4.6629e-15 | 0 | 0
j3 | r17 | t4 | 0 | 1.182e-14 | 0 | 0
j3 | r17 | t5 | 0 | 0 | 0 | 0
j3 | r17 | t6 | 0 | 5.7197e-15 | 0 | 0
j3 | r17 | t7 | 0 | 7.4401e-15 | 0 | 0
j3 | r17 | t8 | 0 | 0 | 0 | 0
j3 | r17 | t9 | 0 | -2.4698e-15 | 0 | 0
j3 | r17 | t10 | 0 | -1.0946e-14 | 0 | 0
j3 | r17 | t11 | 0 | -7.9242e-15 | 0 | 0
j3 | r17 | t12 | 0 | -4.3993e-15 | 0 | 0
j3 | r17 | t13 | 0 | 0 | 0 | 0
j3 | r17 | t14 | 0 | -6.2589e-15 | 0 | 0
j3 | r17 | t15 | 0 | 0 | 0 | 0
j3 | r17 | t16 | 0 | 0 | 0 | 0
j3 | r17 | t17 | 0 | 6.2172e-15 | 0 | 0
j3 | r17 | t18 | 0 | 0 | 0 | 0
j3 | r17 | t19 | 0 | 6.5288e-15 | 0 | 0
j3 | r17 | t20 | 0 | 0 | 0 | 0
j3 | r17 | t21 | 0 | -1.088e-14 | 0 | 0
j3 | r17 | t22 | 0 | 0 | 0 | 0
j3 | r17 | t23 | 0 | 0 | 0 | 0
j3 | r17 | t24 | 0 | 1.0741e-14 | 0 | 0
j3 | r171 | t1 | 0 | -1.3323e-15 | 0 | 0
j3 | r171 | t2 | 0 | 7.816e-14 | 0 | 0
j3 | r171 | t3 | 0 | 0 | 0 | 0
j3 | r171 | t4 | 0 | 2.8422e-14 | 0 | 0
j3 | r171 | t5 | 0 | 0 | 0 | 0
j3 | r171 | t6 | 0 | 0 | 0 | 0
j3 | r171 | t7 | 0 | -3.5527e-14 | 0 | 0
j3 | r171 | t8 | 0 | -7.1054e-15 | 0 | 0
j3 | r171 | t9 | 0 | -1.2212e-14 | 0 | 0
j3 | r171 | t10 | 0 | 9.77e-15 | 0 | 0
j3 | r171 | t11 | 0 | 0 | 0 | 0
j3 | r171 | t12 | 0 | -8.5265e-14 | 0 | 0
j3 | r171 | t13 | 0 | 0 | 0 | 0
j3 | r171 | t14 | 0 | 1.7764e-15 | 0 | 0
j3 | r171 | t15 | 0 | 0 | 0 | 0
j3 | r171 | t16 | 0 | 0 | 0 | 0
j3 | r171 | t17 | 0 | 0 | 0 | 0
j3 | r171 | t18 | 0 | 0 | 0 | 0
j3 | r171 | t19 | 0 | 8.2989e-15 | 0 | 0
j3 | r171 | t20 | 0 | 0 | 0 | 0
j3 | r171 | t21 | 0 | 0 | 0 | 0
j3 | r171 | t22 | 0 | 0 | 0 | 0
j3 | r171 | t23 | 0 | 0 | 0 | 0
j3 | r171 | t24 | 0 | -4.4409e-15 | 0 | 0
j6 | j7 | t1 | 0 | -8.8818e-15 | 0 | 0
j6 | j7 | t2 | 0 | -4.885e-15 | 0 | 0
j6 | j7 | t3 | 0 | -2.4869e-14 | 0 | 0
j6 | j7 | t4 | 0 | -1.1879e-14 | 0 | 0
j6 | j7 | t5 | 0 | 0 | 0 | 0
j6 | j7 | t6 | 0 | -7.5495e-15 | 0 | 0
j6 | j7 | t7 | 0 | 1.2434e-14 | 0 | 0
j6 | j7 | t8 | 0 | 0 | 0 | 0
j6 | j7 | t9 | 0 | -1.1546e-14 | 0 | 0
j6 | j7 | t10 | 0 | -1.3101e-14 | 0 | 0
j6 | j7 | t11 | 0 | -8.8818e-15 | 0 | 0
j6 | j7 | t12 | 0 | -1.1102e-14 | 0 | 0
j6 | j7 | t13 | 0 | -4.4409e-15 | 0 | 0
j6 | j7 | t14 | 0 | 9.2704e-15 | 0 | 0
j6 | j7 | t15 | 0 | 2.6645e-15 | 0 | 0
j6 | j7 | t16 | 0 | 0 | 0 | 0
j6 | j7 | t17 | 0 | -8.7708e-15 | 0 | 0
j6 | j7 | t18 | 0 | 0 | 0 | 0
j6 | j7 | t19 | 0 | 8.4377e-15 | 0 | 0
j6 | j7 | t20 | 0 | 1.3323e-15 | 0 | 0
j6 | j7 | t21 | 0 | 4.1633e-15 | 0 | 0
j6 | j7 | t22 | 0 | 0 | 0 | 0
j6 | j7 | t23 | 0 | -4.885e-15 | 0 | 0
j6 | j7 | t24 | 0 | -3.1086e-15 | 0 | 0
j6 | j10 | t1 | 0 | -2.1316e-14 | 0 | 0
j6 | j10 | t2 | 0 | 3.5527e-14 | 0 | 0
j6 | j10 | t3 | 0 | 0 | 0 | 0
j6 | j10 | t4 | 0 | 0 | 0 | 0
j6 | j10 | t5 | 0 | -1.4211e-14 | 0 | 0
j6 | j10 | t6 | 0 | -2.1316e-14 | 0 | 0
j6 | j10 | t7 | 0 | 1.4003e-14 | 0 | 0
j6 | j10 | t8 | 0 | 2.6645e-15 | 0 | 0
j6 | j10 | t9 | 0 | -1.6209e-14 | 0 | 0
j6 | j10 | t10 | 0 | -4.6629e-15 | 0 | 0
j6 | j10 | t11 | 0 | 0 | 0 | 0
j6 | j10 | t12 | 0 | 0 | 0 | 0
j6 | j10 | t13 | 0 | 1.3545e-14 | 0 | 0
j6 | j10 | t14 | 0 | -1.7764e-15 | 0 | 0
j6 | j10 | t15 | 0 | -1.199e-14 | 0 | 0
j6 | j10 | t16 | 0 | 1.4211e-14 | 0 | 0
j6 | j10 | t17 | 0 | -1.0403e-14 | 0 | 0
j6 | j10 | t18 | 0 | -4.2633e-14 | 0 | 0
j6 | j10 | t19 | 0 | 1.3323e-14 | 0 | 0
j6 | j10 | t20 | 0 | -1.3323e-15 | 0 | 0
j6 | j10 | t21 | 0 | 1.5987e-14 | 0 | 0
j6 | j10 | t22 | 0 | -1.3767e-14 | 0 | 0
j6 | j10 | t23 | 0 | 7.1054e-15 | 0 | 0
j6 | j10 | t24 | 0 | 3.8858e-15 | 0 | 0
j7 | r19 | t1 | 0 | -1.4211e-14 | 0 | 0
j7 | r19 | t2 | 0 | 1.4211e-14 | 0 | 0
j7 | r19 | t3 | 0 | -4.9738e-14 | 0 | 0
j7 | r19 | t4 | 0 | -1.7764e-14 | 0 | 0
j7 | r19 | t5 | 0 | 3.5527e-14 | 0 | 0
j7 | r19 | t6 | 0 | 0 | 0 | 0
j7 | r19 | t7 | 0 | 0 | 0 | 0
j7 | r19 | t8 | 0 | 2.1316e-14 | 0 | 0
j7 | r19 | t9 | 0 | 0 | 0 | 0
j7 | r19 | t10 | 0 | -1.4433e-14 | 0 | 0
j7 | r19 | t11 | 0 | 1.7764e-15 | 0 | 0
j7 | r19 | t12 | 0 | -1.0658e-14 | 0 | 0
j7 | r19 | t13 | 0 | -7.1054e-15 | 0 | 0
j7 | r19 | t14 | 0 | -7.9936e-15 | 0 | 0
j7 | r19 | t15 | 0 | 0 | 0 | 0
j7 | r19 | t16 | 0 | 0 | 0 | 0
j7 | r19 | t17 | 0 | -3.5527e-15 | 0 | 0
j7 | r19 | t18 | 0 | 0 | 0 | 0
j7 | r19 | t19 | 0 | -3.5527e-15 | 0 | 0
j7 | r19 | t20 | 0 | 0 | 0 | 0
j7 | r19 | t21 | 0 | 1.2434e-14 | 0 | 0
j7 | r19 | t22 | 0 | -1.7764e-14 | 0 | 0
j7 | r19 | t23 | 0 | -7.1054e-15 | 0 | 0
j7 | r19 | t24 | 0 | -3.5527e-15 | 0 | 0
j7 | r191 | t1 | 0 | 2.2204e-15 | 0 | 0
j7 | r191 | t2 | 0 | 0 | 0 | 0
j7 | r191 | t3 | 0 | 0 | 0 | 0
j7 | r191 | t4 | 0 | 0 | 0 | 0
j7 | r191 | t5 | 0 | 0 | 0 | 0
j7 | r191 | t6 | 0 | -6.2172e-15 | 0 | 0
j7 | r191 | t7 | 0 | -1.0658e-14 | 0 | 0
j7 | r191 | t8 | 0 | 1.1546e-14 | 0 | 0
j7 | r191 | t9 | 0 | 1.1324e-14 | 0 | 0
j7 | r191 | t10 | 0 | 8.8818e-15 | 0 | 0
j7 | r191 | t11 | 0 | 7.1054e-15 | 0 | 0
j7 | r191 | t12 | 0 | 4.5242e-15 | 0 | 0
j7 | r191 | t13 | 0 | 0 | 0 | 0
j7 | r191 | t14 | 0 | 0 | 0 | 0
j7 | r191 | t15 | 0 | -6.2172e-15 | 0 | 0
j7 | r191 | t16 | 0 | 0 | 0 | 0
j7 | r191 | t17 | 0 | 0 | 0 | 0
j7 | r191 | t18 | 0 | 0 | 0 | 0
j7 | r191 | t19 | 0 | 0 | 0 | 0
j7 | r191 | t20 | 0 | 1.3323e-14 | 0 | 0
j7 | r191 | t21 | 0 | 0 | 0 | 0
j7 | r191 | t22 | 0 | -6.5503e-15 | 0 | 0
j7 | r191 | t23 | 0 | -9.8671e-15 | 0 | 0
j7 | r191 | t24 | 0 | -5.3291e-15 | 0 | 0
j10 | r18 | t1 | 0 | -4.885e-15 | 0 | 0
j10 | r18 | t2 | 0 | 2.8866e-15 | 0 | 0
j10 | r18 | t3 | 0 | 0 | 0 | 0
j10 | r18 | t4 | 0 | 0 | 0 | 0
j10 | r18 | t5 | 0 | 3.5527e-15 | 0 | 0
j10 | r18 | t6 | 0 | 0 | 0 | 0
j10 | r18 | t7 | 0 | 1.3323e-15 | 0 | 0
j10 | r18 | t8 | 0 | -1.3323e-15 | 0 | 0
j10 | r18 | t9 | 0 | 1.1546e-14 | 0 | 0
j10 | r18 | t10 | 0 | 1.1546e-14 | 0 | 0
j10 | r18 | t11 | 0 | 0 | 0 | 0
j10 | r18 | t12 | 0 | 0 | 0 | 0
j10 | r18 | t13 | 0 | 0 | 0 | 0
j10 | r18 | t14 | 0 | -5.3291e-15 | 0 | 0
j10 | r18 | t15 | 0 | -1.0658e-14 | 0 | 0
j10 | r18 | t16 | 0 | 0 | 0 | 0
j10 | r18 | t17 | 0 | 0 | 0 | 0
j10 | r18 | t18 | 0 | 0 | 0 | 0
j10 | r18 | t19 | 0 | 0 | 0 | 0
j10 | r18 | t20 | 0 | -2.8422e-14 | 0 | 0
j10 | r18 | t21 | 0 | 0 | 0 | 0
j10 | r18 | t22 | 0 | 0 | 0 | 0
j10 | r18 | t23 | 0 | 0 | 0 | 0
j10 | r18 | t24 | 0 | 0 | 0 | 0
j10 | r181 | t1 | 0 | -1.7764e-15 | 0 | 0
j10 | r181 | t2 | 0 | 1.4211e-14 | 0 | 0
j10 | r181 | t3 | 0 | 0 | 0 | 0
j10 | r181 | t4 | 0 | 0 | 0 | 0
j10 | r181 | t5 | 0 | -7.1054e-15 | 0 | 0
j10 | r181 | t6 | 0 | 1.0658e-14 | 0 | 0
j10 | r181 | t7 | 0 | 8.9941e-15 | 0 | 0
j10 | r181 | t8 | 0 | -3.9968e-15 | 0 | 0
j10 | r181 | t9 | 0 | -3.1364e-15 | 0 | 0
j10 | r181 | t10 | 0 | -1.3267e-14 | 0 | 0
j10 | r181 | t11 | 0 | 0 | 0 | 0
j10 | r181 | t12 | 0 | 0 | 0 | 0
j10 | r181 | t13 | 0 | -1.0658e-14 | 0 | 0
j10 | r181 | t14 | 0 | 5.3291e-15 | 0 | 0
j10 | r181 | t15 | 0 | 0 | 0 | 0
j10 | r181 | t16 | 0 | 2.1316e-14 | 0 | 0
j10 | r181 | t17 | 0 | -1.3874e-14 | 0 | 0
j10 | r181 | t18 | 0 | -2.4869e-14 | 0 | 0
j10 | r181 | t19 | 0 | 4.4409e-15 | 0 | 0
j10 | r181 | t20 | 0 | 0 | 0 | 0
j10 | r181 | t21 | 0 | -1.5987e-14 | 0 | 0
j10 | r181 | t22 | 0 | -1.3323e-14 | 0 | 0
j10 | r181 | t23 | 0 | 5.3291e-15 | 0 | 0
j10 | r181 | t24 | 0 | 0 | 0 | 0

## phi
TOC
phi | (parameter) | quadratic fit of the pressure loss (m) on the flow (m^3.h^-1) for each pipe
n | n | degree | Value
s | j39 | 1 | 8.57e-05
s | j39 | 2 | 5.9e-06
j39 | j14 | 1 | 0.0003698
j39 | j14 | 2 | 2.93e-05
j39 | j2 | 1 | 0.0002223
j39 | j2 | 2 | 2.51e-05
j14 | j16 | 1 | 0.0003194
j14 | j16 | 2 | 2.53e-05
j14 | r12 | 1 | 0.017434
j14 | r12 | 2 | 0.0072579
j16 | j17 | 1 | 0.0008626
j16 | j17 | 2 | 9.76e-05
j16 | j24 | 1 | 4.2e-06
j16 | j24 | 2 | 6e-07
j17 | j19 | 1 | 0.0014965
j17 | j19 | 2 | 0.0002801
j17 | r13 | 1 | 0.093079
j17 | r13 | 2 | 0.10991
j19 | j21 | 1 | 0.0029922
j19 | j21 | 2 | 0.00056
j19 | r132 | 1 | 0.0025549
j19 | r132 | 2 | 0.0006719
j21 | r133 | 1 | 0.0008234
j21 | r133 | 2 | 0.0001541
j21 | r134 | 1 | 0.00202
j21 | r134 | 2 | 0.000378
j24 | j26 | 1 | 0.0017189
j24 | j26 | 2 | 0.0002442
j24 | r14 | 1 | 0.0005116
j24 | r14 | 2 | 0.0006042
j26 | j27 | 1 | 0.0006496
j26 | j27 | 2 | 9.22e-05
j26 | j30 | 1 | 0.0019744
j26 | j30 | 2 | 0.0002805
j27 | r16 | 1 | 3.86e-05
j27 | r16 | 2 | 5.5e-06
j27 | r161 | 1 | 0.0054486
j27 | r161 | 2 | 0.001433
j30 | r15 | 1 | 0.00192
j30 | r15 | 2 | 0.0005049
j30 | r151 | 1 | 0.0024562
j30 | r151 | 2 | 0.000646
j2 | j3 | 1 | 0.0014572
j2 | j3 | 2 | 0.0006066
j2 | j6 | 1 | 0.0007548
j2 | j6 | 2 | 8.54e-05
j3 | r17 | 1 | 0.0001379
j3 | r17 | 2 | 3.63e-05
j3 | r171 | 1 | 0.01937
j3 | r171 | 2 | 0.0080641
j6 | j7 | 1 | 0.001186
j6 | j7 | 2 | 0.0001341
j6 | j10 | 1 | 0.0024063
j6 | j10 | 2 | 0.0003418
j7 | r19 | 1 | 0.0062146
j7 | r19 | 2 | 0.0016344
j7 | r191 | 1 | 0.001725
j7 | r191 | 2 | 0.0001951
j10 | r18 | 1 | 0.010656
j10 | r18 | 2 | 0.0044362
j10 | r181 | 1 | 0.001646
j10 | r181 | 2 | 0.0003081

## Ppompe
TOC
Ppompe | (variable) | Puissance Ã©lectrique de la pompe (k) Ã (t) en (kW)
c | d | t | Lowerbound | Value | Upperbound | Marginal
small | p1 | t1 | 0 | 39.3341 | INF | 0
small | p1 | t2 | 0 | 39.3384 | INF | 0
small | p1 | t3 | 0 | 39.3398 | INF | 0
small | p1 | t4 | 0 | 39.3404 | INF | 0
small | p1 | t5 | 0 | 39.3411 | INF | 0
small | p1 | t6 | 0 | 39.3055 | INF | 0
small | p1 | t7 | 0 | 39.2243 | INF | 0
small | p1 | t8 | 0 | 39.1027 | INF | 0
small | p1 | t9 | 0 | 54.5265 | INF | 0
small | p1 | t10 | 0 | 52.5132 | INF | 0
small | p1 | t11 | 0 | 43.5527 | INF | 0
small | p1 | t12 | 0 | 43.6132 | INF | 0
small | p1 | t13 | 0 | 43.6794 | INF | 0
small | p1 | t14 | 0 | 43.7296 | INF | 0
small | p1 | t15 | 0 | 43.7763 | INF | 0
small | p1 | t16 | 0 | 43.8166 | INF | 0
small | p1 | t17 | 0 | 43.8567 | INF | 0
small | p1 | t18 | 0 | 43.8766 | INF | 0
small | p1 | t19 | 0 | 43.9129 | INF | 0
small | p1 | t20 | 0 | 43.9373 | INF | 0
small | p1 | t21 | 0 | 43.9625 | INF | 0
small | p1 | t22 | 0 | 43.9169 | INF | 0
small | p1 | t23 | 0 | 43.9296 | INF | 0
small | p1 | t24 | 0 | 43.9506 | INF | 0
small | p2 | t1 | 0 | 39.3341 | INF | 0
small | p2 | t2 | 0 | 39.3384 | INF | 0
small | p2 | t3 | 0 | 39.3398 | INF | 0
small | p2 | t4 | 0 | 39.3404 | INF | 0
small | p2 | t5 | 0 | 39.3411 | INF | 0
small | p2 | t6 | 0 | 39.3055 | INF | 0
small | p2 | t7 | 0 | 39.2243 | INF | 0
small | p2 | t8 | 0 | 39.1027 | INF | 0
small | p2 | t9 | 0 | 54.5265 | INF | 0
small | p2 | t10 | 0 | 52.5132 | INF | 0
small | p2 | t11 | 0 | 43.5527 | INF | 0
small | p2 | t12 | 0 | 43.6132 | INF | 0
small | p2 | t13 | 0 | 43.6794 | INF | 0
small | p2 | t14 | 0 | 43.7296 | INF | 0
small | p2 | t15 | 0 | 43.7763 | INF | 0
small | p2 | t16 | 0 | 43.8166 | INF | 0
small | p2 | t17 | 0 | 43.8567 | INF | 0
small | p2 | t18 | 0 | 43.8766 | INF | 0
small | p2 | t19 | 0 | 43.9129 | INF | 0
small | p2 | t20 | 0 | 43.9373 | INF | 0
small | p2 | t21 | 0 | 43.9625 | INF | 0
small | p2 | t22 | 0 | 43.9169 | INF | 0
small | p2 | t23 | 0 | 43.9296 | INF | 0
small | p2 | t24 | 0 | 43.9506 | INF | 0
large | p1 | t1 | 0 | 145.1046 | INF | 0
large | p1 | t2 | 0 | 145.1054 | INF | 0
large | p1 | t3 | 0 | 110.3429 | INF | 0
large | p1 | t4 | 0 | 145.1058 | INF | 0
large | p1 | t5 | 0 | 145.1059 | INF | 0
large | p1 | t6 | 0 | 145.0995 | INF | 0
large | p1 | t7 | 0 | 96.0117 | INF | 0
large | p1 | t8 | 0 | 145.064 | INF | 0
large | p1 | t9 | 0 | 77.3794 | INF | 0
large | p1 | t10 | 0 | 133.6445 | INF | 0
large | p1 | t11 | 0 | 146.264 | INF | 0
large | p1 | t12 | 0 | 146.2862 | INF | 0
large | p1 | t13 | 0 | 77.3794 | INF | 0
large | p1 | t14 | 0 | 123.1726 | INF | 0
large | p1 | t15 | 0 | 123.7081 | INF | 0
large | p1 | t16 | 0 | 146.3624 | INF | 0
large | p1 | t17 | 0 | 146.3776 | INF | 0
large | p1 | t18 | 0 | 114.7948 | INF | 0
large | p1 | t19 | 0 | 126.8801 | INF | 0
large | p1 | t20 | 0 | 146.4084 | INF | 0
large | p1 | t21 | 0 | 94.8329 | INF | 0
large | p1 | t22 | 0 | 146.4006 | INF | 0
large | p1 | t23 | 0 | 146.4055 | INF | 0
large | p1 | t24 | 0 | 145.1311 | INF | 0
large | p2 | t1 | 0 | 145.1046 | INF | 0
large | p2 | t2 | 0 | 145.1054 | INF | 0
large | p2 | t3 | 0 | 110.3429 | INF | 0
large | p2 | t4 | 0 | 145.1058 | INF | 0
large | p2 | t5 | 0 | 140.8355 | INF | 0
large | p2 | t6 | 0 | 145.0995 | INF | 0
large | p2 | t7 | 0 | 145.0851 | INF | 0
large | p2 | t8 | 0 | 132.6682 | INF | 0
large | p2 | t9 | 0 | 99.8642 | INF | 0
large | p2 | t10 | 0 | 79.6208 | INF | 0
large | p2 | t11 | 0 | 112.5033 | INF | 0
large | p2 | t12 | 0 | 80.289 | INF | 0
large | p2 | t13 | 0 | 122.9695 | INF | 0
large | p2 | t14 | 0 | 146.3296 | INF | 0
large | p2 | t15 | 0 | 146.3472 | INF | 0
large | p2 | t16 | 0 | 94.3907 | INF | 0
large | p2 | t17 | 0 | 108.8666 | INF | 0
large | p2 | t18 | 0 | 123.1082 | INF | 0
large | p2 | t19 | 0 | 145.343 | INF | 0
large | p2 | t20 | 0 | 122.2926 | INF | 0
large | p2 | t21 | 0 | 146.4181 | INF | 0
large | p2 | t22 | 0 | 109.5072 | INF | 0
large | p2 | t23 | 0 | 102.8295 | INF | 0
large | p2 | t24 | 0 | 94.1275 | INF | 0
large | p3 | t1 | 0 | 108.3018 | INF | 0
large | p3 | t2 | 0 | 101.1414 | INF | 0
large | p3 | t3 | 0 | 110.3429 | INF | 0
large | p3 | t4 | 0 | 94.8547 | INF | 0
large | p3 | t5 | 0 | 102.0201 | INF | 0
large | p3 | t6 | 0 | 84.9038 | INF | 0
large | p3 | t7 | 0 | 85.0062 | INF | 0
large | p3 | t8 | 0 | 77.3794 | INF | 0
large | p3 | t9 | 0 | 77.3794 | INF | 0
large | p3 | t10 | 0 | 79.6208 | INF | 0
large | p3 | t11 | 0 | 81.5673 | INF | 0
large | p3 | t12 | 0 | 84.8183 | INF | 0
large | p3 | t13 | 0 | 140.7551 | INF | 0
large | p3 | t14 | 0 | 77.5143 | INF | 0
large | p3 | t15 | 0 | 77.3794 | INF | 0
large | p3 | t16 | 0 | 92.4351 | INF | 0
large | p3 | t17 | 0 | 85.4724 | INF | 0
large | p3 | t18 | 0 | 94.2838 | INF | 0
large | p3 | t19 | 0 | 77.3794 | INF | 0
large | p3 | t20 | 0 | 77.3794 | INF | 0
large | p3 | t21 | 0 | 93.2153 | INF | 0
large | p3 | t22 | 0 | 85.5652 | INF | 0
large | p3 | t23 | 0 | 88.9916 | INF | 0
large | p3 | t24 | 0 | 94.1275 | INF | 0
large | p4 | t1 | 0 | 77.3794 | INF | 0
large | p4 | t2 | 0 | 84.7202 | INF | 0
large | p4 | t3 | 0 | 145.1056 | INF | 0
large | p4 | t4 | 0 | 91.092 | INF | 0
large | p4 | t5 | 0 | 88.2257 | INF | 0
large | p4 | t6 | 0 | 99.561 | INF | 0
large | p4 | t7 | 0 | 145.0851 | INF | 0
large | p4 | t8 | 0 | 110.8696 | INF | 0
large | p4 | t9 | 0 | 77.3794 | INF | 0
large | p4 | t10 | 0 | 79.6208 | INF | 0
large | p4 | t11 | 0 | 81.5673 | INF | 0
large | p4 | t12 | 0 | 111.3604 | INF | 0
large | p4 | t13 | 0 | 82.5847 | INF | 0
large | p4 | t14 | 0 | 77.3794 | INF | 0
large | p4 | t15 | 0 | 77.6203 | INF | 0
large | p4 | t16 | 0 | 92.4351 | INF | 0
large | p4 | t17 | 0 | 85.4724 | INF | 0
large | p4 | t18 | 0 | 94.2838 | INF | 0
large | p4 | t19 | 0 | 77.3794 | INF | 0
large | p4 | t20 | 0 | 81.2459 | INF | 0
large | p4 | t21 | 0 | 93.2153 | INF | 0
large | p4 | t22 | 0 | 85.5652 | INF | 0
large | p4 | t23 | 0 | 88.9916 | INF | 0
large | p4 | t24 | 0 | 94.1275 | INF | 0

## psi
TOC
psi | (parameter) | quadratic fit of the service pressure (m) on the flow (m^3.h^-1) for each class of pumps
c | degree | Value
small | 0 | 152.3245
small | 2 | -0.0010392
large | 0 | 178.3516
large | 2 | -0.00037

## Qmax
TOC
Qmax | (parameter) | DÃ©bit maximum
c | d | Value
small | p1 | 382.8559
small | p2 | 382.8559
large | p1 | 694.2848
large | p2 | 694.2848
large | p3 | 694.2848
large | p4 | 694.2848

## Qmin
TOC
Qmin | (parameter) | DÃ©bit minimum
c | d | Value
small | p1 | 1
small | p2 | 1
large | p1 | 1
large | p2 | 1
large | p3 | 1
large | p4 | 1

## Qpipe
TOC
Qpipe | (variable) | DÃ©bit dans le tuyau (l) Ã (t)
n | n | t | Lowerbound | Value | Upperbound | Marginal
s | j39 | t1 | 0 | 689.1536 | INF | 0
s | j39 | t2 | 0 | 689.9022 | INF | 0
s | j39 | t3 | 0 | 690.1577 | INF | 0
s | j39 | t4 | 0 | 690.2557 | INF | 0
s | j39 | t5 | 0 | 690.3746 | INF | 0
s | j39 | t6 | 0 | 684.1058 | INF | 0
s | j39 | t7 | 0 | 669.8039 | INF | 0
s | j39 | t8 | 0 | 648.3786 | INF | 0
s | j39 | t9 | 0 | 250.1721 | INF | 0
s | j39 | t10 | 0 | 392.4227 | INF | 0
s | j39 | t11 | 0 | 512.2143 | INF | 0
s | j39 | t12 | 0 | 516.0554 | INF | 0
s | j39 | t13 | 0 | 520.2683 | INF | 0
s | j39 | t14 | 0 | 523.4557 | INF | 0
s | j39 | t15 | 0 | 526.4266 | INF | 0
s | j39 | t16 | 0 | 528.988 | INF | 0
s | j39 | t17 | 0 | 531.5373 | INF | 0
s | j39 | t18 | 0 | 532.8074 | INF | 0
s | j39 | t19 | 0 | 535.1114 | INF | 0
s | j39 | t20 | 0 | 536.6639 | INF | 0
s | j39 | t21 | 0 | 538.2652 | INF | 0
s | j39 | t22 | 0 | 535.3648 | INF | 0
s | j39 | t23 | 0 | 536.1763 | INF | 0
s | j39 | t24 | 0 | 537.5086 | INF | 0
j39 | j14 | t1 | 0 | 290.6478 | INF | 0
j39 | j14 | t2 | 0 | 290.967 | INF | 0
j39 | j14 | t3 | 0 | 291.076 | INF | 0
j39 | j14 | t4 | 0 | 291.1177 | INF | 0
j39 | j14 | t5 | 0 | 291.1685 | INF | 0
j39 | j14 | t6 | 0 | 288.4953 | INF | 0
j39 | j14 | t7 | 0 | 282.3969 | INF | 0
j39 | j14 | t8 | 0 | 273.2609 | INF | 0
j39 | j14 | t9 | 0 | 115.5021 | INF | 0
j39 | j14 | t10 | 0 | 205.7627 | INF | 0
j39 | j14 | t11 | 0 | 281.3086 | INF | 0
j39 | j14 | t12 | 0 | 283.4354 | INF | 0
j39 | j14 | t13 | 0 | 285.7679 | INF | 0
j39 | j14 | t14 | 0 | 287.5327 | INF | 0
j39 | j14 | t15 | 0 | 289.1776 | INF | 0
j39 | j14 | t16 | 0 | 290.5958 | INF | 0
j39 | j14 | t17 | 0 | 292.0072 | INF | 0
j39 | j14 | t18 | 0 | 292.7105 | INF | 0
j39 | j14 | t19 | 0 | 293.9861 | INF | 0
j39 | j14 | t20 | 0 | 294.8457 | INF | 0
j39 | j14 | t21 | 0 | 295.7323 | INF | 0
j39 | j14 | t22 | 0 | 294.1264 | INF | 0
j39 | j14 | t23 | 0 | 294.5757 | INF | 0
j39 | j14 | t24 | 0 | 295.3133 | INF | 0
j39 | j2 | t1 | 0 | 398.5058 | INF | 0
j39 | j2 | t2 | 0 | 398.9352 | INF | 0
j39 | j2 | t3 | 0 | 399.0818 | INF | 0
j39 | j2 | t4 | 0 | 399.1379 | INF | 0
j39 | j2 | t5 | 0 | 399.2062 | INF | 0
j39 | j2 | t6 | 0 | 395.6104 | INF | 0
j39 | j2 | t7 | 0 | 387.407 | INF | 0
j39 | j2 | t8 | 0 | 375.1176 | INF | 0
j39 | j2 | t9 | 0 | 134.67 | INF | 0
j39 | j2 | t10 | 0 | 186.66 | INF | 0
j39 | j2 | t11 | 0 | 230.9056 | INF | 0
j39 | j2 | t12 | 0 | 232.62 | INF | 0
j39 | j2 | t13 | 0 | 234.5004 | INF | 0
j39 | j2 | t14 | 0 | 235.923 | INF | 0
j39 | j2 | t15 | 0 | 237.249 | INF | 0
j39 | j2 | t16 | 0 | 238.3922 | INF | 0
j39 | j2 | t17 | 0 | 239.5301 | INF | 0
j39 | j2 | t18 | 0 | 240.097 | INF | 0
j39 | j2 | t19 | 0 | 241.1253 | INF | 0
j39 | j2 | t20 | 0 | 241.8182 | INF | 0
j39 | j2 | t21 | 0 | 242.5329 | INF | 0
j39 | j2 | t22 | 0 | 241.2384 | INF | 0
j39 | j2 | t23 | 0 | 241.6006 | INF | 0
j39 | j2 | t24 | 0 | 242.1952 | INF | 0
j14 | j16 | t1 | 0 | 274.0381 | INF | 0
j14 | j16 | t2 | 0 | 274.3395 | INF | 0
j14 | j16 | t3 | 0 | 274.4424 | INF | 0
j14 | j16 | t4 | 0 | 274.4818 | INF | 0
j14 | j16 | t5 | 0 | 274.5297 | INF | 0
j14 | j16 | t6 | 0 | 272.0061 | INF | 0
j14 | j16 | t7 | 0 | 266.2487 | INF | 0
j14 | j16 | t8 | 0 | 257.6237 | INF | 0
j14 | j16 | t9 | 0 | 112.5021 | INF | 0
j14 | j16 | t10 | 0 | 196.5927 | INF | 0
j14 | j16 | t11 | 0 | 269.8238 | INF | 0
j14 | j16 | t12 | 0 | 271.8656 | INF | 0
j14 | j16 | t13 | 0 | 274.105 | INF | 0
j14 | j16 | t14 | 0 | 275.7993 | INF | 0
j14 | j16 | t15 | 0 | 277.3785 | INF | 0
j14 | j16 | t16 | 0 | 278.7401 | INF | 0
j14 | j16 | t17 | 0 | 280.0952 | INF | 0
j14 | j16 | t18 | 0 | 280.7704 | INF | 0
j14 | j16 | t19 | 0 | 281.9951 | INF | 0
j14 | j16 | t20 | 0 | 282.8204 | INF | 0
j14 | j16 | t21 | 0 | 283.6716 | INF | 0
j14 | j16 | t22 | 0 | 282.1298 | INF | 0
j14 | j16 | t23 | 0 | 282.5611 | INF | 0
j14 | j16 | t24 | 0 | 283.2693 | INF | 0
j14 | r12 | t1 | 0 | 16.6096 | INF | 0
j14 | r12 | t2 | 0 | 16.6275 | INF | 0
j14 | r12 | t3 | 0 | 16.6336 | INF | 0
j14 | r12 | t4 | 0 | 16.6359 | INF | 0
j14 | r12 | t5 | 0 | 16.6387 | INF | 0
j14 | r12 | t6 | 0 | 16.4892 | INF | 0
j14 | r12 | t7 | 0 | 16.1482 | INF | 0
j14 | r12 | t8 | 0 | 15.6372 | INF | 0
j14 | r12 | t9 | 0 | 3 | INF | 0
j14 | r12 | t10 | 0 | 9.17 | INF | 0
j14 | r12 | t11 | 0 | 11.4849 | INF | 0
j14 | r12 | t12 | 0 | 11.5698 | INF | 0
j14 | r12 | t13 | 0 | 11.6629 | INF | 0
j14 | r12 | t14 | 0 | 11.7334 | INF | 0
j14 | r12 | t15 | 0 | 11.799 | INF | 0
j14 | r12 | t16 | 0 | 11.8557 | INF | 0
j14 | r12 | t17 | 0 | 11.912 | INF | 0
j14 | r12 | t18 | 0 | 11.9401 | INF | 0
j14 | r12 | t19 | 0 | 11.991 | INF | 0
j14 | r12 | t20 | 0 | 12.0253 | INF | 0
j14 | r12 | t21 | 0 | 12.0607 | INF | 0
j14 | r12 | t22 | 0 | 11.9966 | INF | 0
j14 | r12 | t23 | 0 | 12.0146 | INF | 0
j14 | r12 | t24 | 0 | 12.044 | INF | 0
j16 | j17 | t1 | 0 | 116.8964 | INF | 0
j16 | j17 | t2 | 0 | 117.0268 | INF | 0
j16 | j17 | t3 | 0 | 117.0713 | INF | 0
j16 | j17 | t4 | 0 | 117.0884 | INF | 0
j16 | j17 | t5 | 0 | 117.1091 | INF | 0
j16 | j17 | t6 | 0 | 116.0171 | INF | 0
j16 | j17 | t7 | 0 | 113.5257 | INF | 0
j16 | j17 | t8 | 0 | 109.7934 | INF | 0
j16 | j17 | t9 | 0 | 82.3321 | INF | 0
j16 | j17 | t10 | 0 | 85.5827 | INF | 0
j16 | j17 | t11 | 0 | 100.214 | INF | 0
j16 | j17 | t12 | 0 | 100.9781 | INF | 0
j16 | j17 | t13 | 0 | 101.8162 | INF | 0
j16 | j17 | t14 | 0 | 102.4502 | INF | 0
j16 | j17 | t15 | 0 | 103.0412 | INF | 0
j16 | j17 | t16 | 0 | 103.5507 | INF | 0
j16 | j17 | t17 | 0 | 104.0579 | INF | 0
j16 | j17 | t18 | 0 | 104.3105 | INF | 0
j16 | j17 | t19 | 0 | 104.7688 | INF | 0
j16 | j17 | t20 | 0 | 105.0777 | INF | 0
j16 | j17 | t21 | 0 | 105.3962 | INF | 0
j16 | j17 | t22 | 0 | 104.8193 | INF | 0
j16 | j17 | t23 | 0 | 104.9807 | INF | 0
j16 | j17 | t24 | 0 | 105.2457 | INF | 0
j16 | j24 | t1 | 0 | 157.1418 | INF | 0
j16 | j24 | t2 | 0 | 157.3127 | INF | 0
j16 | j24 | t3 | 0 | 157.3711 | INF | 0
j16 | j24 | t4 | 0 | 157.3934 | INF | 0
j16 | j24 | t5 | 0 | 157.4206 | INF | 0
j16 | j24 | t6 | 0 | 155.989 | INF | 0
j16 | j24 | t7 | 0 | 152.723 | INF | 0
j16 | j24 | t8 | 0 | 147.8303 | INF | 0
j16 | j24 | t9 | 0 | 30.17 | INF | 0
j16 | j24 | t10 | 0 | 111.01 | INF | 0
j16 | j24 | t11 | 0 | 169.6097 | INF | 0
j16 | j24 | t12 | 0 | 170.8875 | INF | 0
j16 | j24 | t13 | 0 | 172.2888 | INF | 0
j16 | j24 | t14 | 0 | 173.3491 | INF | 0
j16 | j24 | t15 | 0 | 174.3373 | INF | 0
j16 | j24 | t16 | 0 | 175.1894 | INF | 0
j16 | j24 | t17 | 0 | 176.0374 | INF | 0
j16 | j24 | t18 | 0 | 176.4599 | INF | 0
j16 | j24 | t19 | 0 | 177.2263 | INF | 0
j16 | j24 | t20 | 0 | 177.7427 | INF | 0
j16 | j24 | t21 | 0 | 178.2753 | INF | 0
j16 | j24 | t22 | 0 | 177.3106 | INF | 0
j16 | j24 | t23 | 0 | 177.5805 | INF | 0
j16 | j24 | t24 | 0 | 178.0236 | INF | 0
j17 | j19 | t1 | 0 | 110.0319 | INF | 0
j17 | j19 | t2 | 0 | 110.1531 | INF | 0
j17 | j19 | t3 | 0 | 110.1944 | INF | 0
j17 | j19 | t4 | 0 | 110.2103 | INF | 0
j17 | j19 | t5 | 0 | 110.2296 | INF | 0
j17 | j19 | t6 | 0 | 109.215 | INF | 0
j17 | j19 | t7 | 0 | 106.9005 | INF | 0
j17 | j19 | t8 | 0 | 103.4332 | INF | 0
j17 | j19 | t9 | 0 | 82.3321 | INF | 0
j17 | j19 | t10 | 0 | 85.5827 | INF | 0
j17 | j19 | t11 | 0 | 100.214 | INF | 0
j17 | j19 | t12 | 0 | 100.9781 | INF | 0
j17 | j19 | t13 | 0 | 101.8162 | INF | 0
j17 | j19 | t14 | 0 | 102.4502 | INF | 0
j17 | j19 | t15 | 0 | 103.0412 | INF | 0
j17 | j19 | t16 | 0 | 103.5507 | INF | 0
j17 | j19 | t17 | 0 | 104.0579 | INF | 0
j17 | j19 | t18 | 0 | 104.3105 | INF | 0
j17 | j19 | t19 | 0 | 104.7688 | INF | 0
j17 | j19 | t20 | 0 | 105.0777 | INF | 0
j17 | j19 | t21 | 0 | 105.3962 | INF | 0
j17 | j19 | t22 | 0 | 104.8193 | INF | 0
j17 | j19 | t23 | 0 | 104.9807 | INF | 0
j17 | j19 | t24 | 0 | 105.2457 | INF | 0
j17 | r13 | t1 | 0 | 6.8644 | INF | 0
j17 | r13 | t2 | 0 | 6.8737 | INF | 0
j17 | r13 | t3 | 0 | 6.8769 | INF | 0
j17 | r13 | t4 | 0 | 6.8781 | INF | 0
j17 | r13 | t5 | 0 | 6.8795 | INF | 0
j17 | r13 | t6 | 0 | 6.802 | INF | 0
j17 | r13 | t7 | 0 | 6.6252 | INF | 0
j17 | r13 | t8 | 0 | 6.3602 | INF | 0
j17 | r13 | t9 | 0 | 0 | INF | 0.0031746
j17 | r13 | t10 | 0 | 0 | INF | 0.0032959
j17 | r13 | t11 | 0 | 0 | INF | 0.0038913
j17 | r13 | t12 | 0 | 0 | INF | 0.0038913
j17 | r13 | t13 | 0 | 0 | INF | 0.0038913
j17 | r13 | t14 | 0 | 0 | INF | 0.0038912
j17 | r13 | t15 | 0 | 0 | INF | 0.0038912
j17 | r13 | t16 | 0 | 0 | INF | 0.0038912
j17 | r13 | t17 | 0 | 0 | INF | 0.0038912
j17 | r13 | t18 | 0 | 0 | INF | 0.0038912
j17 | r13 | t19 | 0 | 0 | INF | 0.0038911
j17 | r13 | t20 | 0 | 0 | INF | 0.0038911
j17 | r13 | t21 | 0 | 0 | INF | 0.0038911
j17 | r13 | t22 | 0 | 0 | INF | 0.0038911
j17 | r13 | t23 | 0 | 0 | INF | 0.0038911
j17 | r13 | t24 | 0 | 0 | INF | 0.0038911
j19 | j21 | t1 | 0 | 75.981 | INF | 0
j19 | j21 | t2 | 0 | 76.0656 | INF | 0
j19 | j21 | t3 | 0 | 76.0945 | INF | 0
j19 | j21 | t4 | 0 | 76.1055 | INF | 0
j19 | j21 | t5 | 0 | 76.119 | INF | 0
j19 | j21 | t6 | 0 | 75.411 | INF | 0
j19 | j21 | t7 | 0 | 73.7957 | INF | 0
j19 | j21 | t8 | 0 | 71.8128 | INF | 0
j19 | j21 | t9 | 0 | 75.8321 | INF | 0
j19 | j21 | t10 | 0 | 68.5827 | INF | 0
j19 | j21 | t11 | 0 | 76.878 | INF | 0
j19 | j21 | t12 | 0 | 77.4662 | INF | 0
j19 | j21 | t13 | 0 | 78.1113 | INF | 0
j19 | j21 | t14 | 0 | 78.5994 | INF | 0
j19 | j21 | t15 | 0 | 79.0544 | INF | 0
j19 | j21 | t16 | 0 | 79.4466 | INF | 0
j19 | j21 | t17 | 0 | 79.837 | INF | 0
j19 | j21 | t18 | 0 | 80.0315 | INF | 0
j19 | j21 | t19 | 0 | 80.3843 | INF | 0
j19 | j21 | t20 | 0 | 80.6221 | INF | 0
j19 | j21 | t21 | 0 | 80.8673 | INF | 0
j19 | j21 | t22 | 0 | 80.4231 | INF | 0
j19 | j21 | t23 | 0 | 80.5474 | INF | 0
j19 | j21 | t24 | 0 | 80.7514 | INF | 0
j19 | r132 | t1 | 0 | 34.0509 | INF | 0
j19 | r132 | t2 | 0 | 34.0875 | INF | 0
j19 | r132 | t3 | 0 | 34.1 | INF | 0
j19 | r132 | t4 | 0 | 34.1048 | INF | 0
j19 | r132 | t5 | 0 | 34.1106 | INF | 0
j19 | r132 | t6 | 0 | 33.8041 | INF | 0
j19 | r132 | t7 | 0 | 33.1048 | INF | 0
j19 | r132 | t8 | 0 | 31.6204 | INF | 0
j19 | r132 | t9 | 0 | 6.5 | INF | 0
j19 | r132 | t10 | 0 | 17 | INF | 0
j19 | r132 | t11 | 0 | 23.336 | INF | 0
j19 | r132 | t12 | 0 | 23.5119 | INF | 0
j19 | r132 | t13 | 0 | 23.7048 | INF | 0
j19 | r132 | t14 | 0 | 23.8508 | INF | 0
j19 | r132 | t15 | 0 | 23.9868 | INF | 0
j19 | r132 | t16 | 0 | 24.1041 | INF | 0
j19 | r132 | t17 | 0 | 24.2208 | INF | 0
j19 | r132 | t18 | 0 | 24.279 | INF | 0
j19 | r132 | t19 | 0 | 24.3845 | INF | 0
j19 | r132 | t20 | 0 | 24.4556 | INF | 0
j19 | r132 | t21 | 0 | 24.5289 | INF | 0
j19 | r132 | t22 | 0 | 24.3961 | INF | 0
j19 | r132 | t23 | 0 | 24.4333 | INF | 0
j19 | r132 | t24 | 0 | 24.4943 | INF | 0
j21 | r133 | t1 | 0 | 65.151 | INF | 0
j21 | r133 | t2 | 0 | 69.2356 | INF | 0
j21 | r133 | t3 | 0 | 71.0945 | INF | 0
j21 | r133 | t4 | 0 | 71.9355 | INF | 0
j21 | r133 | t5 | 0 | 73.119 | INF | 0
j21 | r133 | t6 | 0 | 57.5092 | INF | 0
j21 | r133 | t7 | 0 | 41.4402 | INF | 0
j21 | r133 | t8 | 0 | 26.5 | INF | 0
j21 | r133 | t9 | 0 | 30.67 | INF | 0
j21 | r133 | t10 | 0 | 45.67 | INF | 0
j21 | r133 | t11 | 0 | 76.878 | INF | 0
j21 | r133 | t12 | 0 | 77.4662 | INF | 0
j21 | r133 | t13 | 0 | 78.1113 | INF | 0
j21 | r133 | t14 | 0 | 78.5994 | INF | 0
j21 | r133 | t15 | 0 | 79.0544 | INF | 0
j21 | r133 | t16 | 0 | 79.4466 | INF | 0
j21 | r133 | t17 | 0 | 79.837 | INF | 0
j21 | r133 | t18 | 0 | 80.0315 | INF | 0
j21 | r133 | t19 | 0 | 80.3843 | INF | 0
j21 | r133 | t20 | 0 | 80.6221 | INF | 0
j21 | r133 | t21 | 0 | 75.8521 | INF | 0
j21 | r133 | t22 | 0 | 60.4231 | INF | 0
j21 | r133 | t23 | 0 | 63.5474 | INF | 0
j21 | r133 | t24 | 0 | 70.0814 | INF | 0
j21 | r134 | t1 | 0 | 10.83 | INF | 0
j21 | r134 | t2 | 0 | 6.83 | INF | 0
j21 | r134 | t3 | 0 | 5 | INF | 0
j21 | r134 | t4 | 0 | 4.17 | INF | 0
j21 | r134 | t5 | 0 | 3 | INF | 0
j21 | r134 | t6 | 0 | 17.9017 | INF | 0
j21 | r134 | t7 | 0 | 32.3555 | INF | 0
j21 | r134 | t8 | 0 | 45.3128 | INF | 0
j21 | r134 | t9 | 0 | 45.1621 | INF | 0
j21 | r134 | t10 | 0 | 22.9127 | INF | 0
j21 | r134 | t11 | 0 | 0 | INF | 0.0017954
j21 | r134 | t12 | 0 | 0 | INF | 0.0016048
j21 | r134 | t13 | 0 | 0 | INF | 0.0014155
j21 | r134 | t14 | 0 | 0 | INF | 0.0012279
j21 | r134 | t15 | 0 | 0 | INF | 0.0010414
j21 | r134 | t16 | 0 | 0 | INF | 0.00085592
j21 | r134 | t17 | 0 | 0 | INF | 0.00067135
j21 | r134 | t18 | 0 | 0 | INF | 0.00048774
j21 | r134 | t19 | 0 | 0 | INF | 0.00030449
j21 | r134 | t20 | 0 | 0 | INF | 0.00012207
j21 | r134 | t21 | 0 | 5.0152 | INF | 0
j21 | r134 | t22 | 0 | 20 | INF | 0
j21 | r134 | t23 | 0 | 17 | INF | 0
j21 | r134 | t24 | 0 | 10.67 | INF | 0
j24 | j26 | t1 | 0 | 155.8918 | INF | 0
j24 | j26 | t2 | 0 | 157.3127 | INF | 0
j24 | j26 | t3 | 0 | 157.3711 | INF | 0
j24 | j26 | t4 | 0 | 157.3934 | INF | 0
j24 | j26 | t5 | 0 | 136.8409 | INF | 0
j24 | j26 | t6 | 0 | 142.5151 | INF | 0
j24 | j26 | t7 | 0 | 152.723 | INF | 0
j24 | j26 | t8 | 0 | 136.384 | INF | 0
j24 | j26 | t9 | 0 | 30.17 | INF | 0
j24 | j26 | t10 | 0 | 107.01 | INF | 0
j24 | j26 | t11 | 0 | 169.6097 | INF | 0
j24 | j26 | t12 | 0 | 170.8875 | INF | 0
j24 | j26 | t13 | 0 | 172.2888 | INF | 0
j24 | j26 | t14 | 0 | 173.3491 | INF | 0
j24 | j26 | t15 | 0 | 160.606 | INF | 0
j24 | j26 | t16 | 0 | 175.1894 | INF | 0
j24 | j26 | t17 | 0 | 176.0374 | INF | 0
j24 | j26 | t18 | 0 | 176.4599 | INF | 0
j24 | j26 | t19 | 0 | 177.2263 | INF | 0
j24 | j26 | t20 | 0 | 177.7427 | INF | 0
j24 | j26 | t21 | 0 | 178.2753 | INF | 0
j24 | j26 | t22 | 0 | 177.3106 | INF | 0
j24 | j26 | t23 | 0 | 177.5805 | INF | 0
j24 | j26 | t24 | 0 | 175.005 | INF | 0
j24 | r14 | t1 | 0 | 1.25 | INF | 0
j24 | r14 | t2 | 0 | 0 | INF | 0
j24 | r14 | t3 | 0 | 0 | INF | 0
j24 | r14 | t4 | 0 | 0 | INF | 0
j24 | r14 | t5 | 0 | 20.5797 | INF | 0
j24 | r14 | t6 | 0 | 13.474 | INF | 0
j24 | r14 | t7 | 0 | 0 | INF | 0
j24 | r14 | t8 | 0 | 11.4464 | INF | 0
j24 | r14 | t9 | 0 | 0 | INF | 0
j24 | r14 | t10 | 0 | 4 | INF | 0
j24 | r14 | t11 | 0 | 0 | INF | 0
j24 | r14 | t12 | 0 | 0 | INF | 0
j24 | r14 | t13 | 0 | 0 | INF | 0
j24 | r14 | t14 | 0 | 0 | INF | 0
j24 | r14 | t15 | 0 | 13.7313 | INF | 0
j24 | r14 | t16 | 0 | 0 | INF | 0
j24 | r14 | t17 | 0 | 0 | INF | 0
j24 | r14 | t18 | 0 | 0 | INF | 0
j24 | r14 | t19 | 0 | 0 | INF | 0
j24 | r14 | t20 | 0 | 0 | INF | 0
j24 | r14 | t21 | 0 | 0 | INF | 0
j24 | r14 | t22 | 0 | 0 | INF | 0
j24 | r14 | t23 | 0 | 0 | INF | 0
j24 | r14 | t24 | 0 | 3.0187 | INF | 0
j26 | j27 | t1 | 0 | 60.33 | INF | 0
j26 | j27 | t2 | 0 | 117.7586 | INF | 0
j26 | j27 | t3 | 0 | 146.817 | INF | 0
j26 | j27 | t4 | 0 | 0 | INF | 0
j26 | j27 | t5 | 0 | 10.6409 | INF | 0
j26 | j27 | t6 | 0 | 0 | INF | 0
j26 | j27 | t7 | 0 | 152.723 | INF | 0
j26 | j27 | t8 | 0 | 22.0895 | INF | 0
j26 | j27 | t9 | 0 | 6.17 | INF | 0
j26 | j27 | t10 | 0 | 51.84 | INF | 0
j26 | j27 | t11 | 0 | 70 | INF | 0
j26 | j27 | t12 | 0 | 0 | INF | 0
j26 | j27 | t13 | 0 | 172.2888 | INF | 0
j26 | j27 | t14 | 0 | 105.1012 | INF | 0
j26 | j27 | t15 | 0 | 55.1744 | INF | 0
j26 | j27 | t16 | 0 | 3.4792 | INF | 0
j26 | j27 | t17 | 0 | 176.0374 | INF | 0
j26 | j27 | t18 | 0 | 16.89 | INF | 0
j26 | j27 | t19 | 0 | 0 | INF | 0
j26 | j27 | t20 | 0 | 177.7427 | INF | 0
j26 | j27 | t21 | 0 | 15.2573 | INF | 0
j26 | j27 | t22 | 0 | 136.1069 | INF | 0
j26 | j27 | t23 | 0 | 73.5743 | INF | 0
j26 | j27 | t24 | 0 | 78.9788 | INF | 0
j26 | j30 | t1 | 0 | 95.5618 | INF | 0
j26 | j30 | t2 | 0 | 39.5541 | INF | 0
j26 | j30 | t3 | 0 | 10.5541 | INF | 0
j26 | j30 | t4 | 0 | 157.3934 | INF | 0
j26 | j30 | t5 | 0 | 126.2 | INF | 0
j26 | j30 | t6 | 0 | 142.5151 | INF | 0
j26 | j30 | t7 | 0 | 0 | INF | 0
j26 | j30 | t8 | 0 | 114.2945 | INF | 0
j26 | j30 | t9 | 0 | 24 | INF | 0
j26 | j30 | t10 | 0 | 55.17 | INF | 0
j26 | j30 | t11 | 0 | 99.6097 | INF | 0
j26 | j30 | t12 | 0 | 170.8875 | INF | 0
j26 | j30 | t13 | 0 | 0 | INF | 0
j26 | j30 | t14 | 0 | 68.2479 | INF | 0
j26 | j30 | t15 | 0 | 105.4316 | INF | 0
j26 | j30 | t16 | 0 | 171.7101 | INF | 0
j26 | j30 | t17 | 0 | 0 | INF | 0
j26 | j30 | t18 | 0 | 159.5698 | INF | 0
j26 | j30 | t19 | 0 | 177.2263 | INF | 0
j26 | j30 | t20 | 0 | 0 | INF | 0
j26 | j30 | t21 | 0 | 163.018 | INF | 0
j26 | j30 | t22 | 0 | 41.2037 | INF | 0
j26 | j30 | t23 | 0 | 104.0062 | INF | 0
j26 | j30 | t24 | 0 | 96.0261 | INF | 0
j27 | r16 | t1 | 0 | 13 | INF | 0
j27 | r16 | t2 | 0 | 12 | INF | 0
j27 | r16 | t3 | 0 | 15 | INF | 0
j27 | r16 | t4 | 0 | 0 | INF | 0
j27 | r16 | t5 | 0 | 10.0511 | INF | 0
j27 | r16 | t6 | 0 | 0 | INF | 0
j27 | r16 | t7 | 0 | 43.5489 | INF | 0
j27 | r16 | t8 | 0 | 2 | INF | 0
j27 | r16 | t9 | 0 | 2.17 | INF | 0
j27 | r16 | t10 | 0 | 9.17 | INF | 0
j27 | r16 | t11 | 0 | 10 | INF | 0
j27 | r16 | t12 | 0 | 0 | INF | 0
j27 | r16 | t13 | 0 | 19.23 | INF | 0
j27 | r16 | t14 | 0 | 0 | INF | 0
j27 | r16 | t15 | 0 | 0 | INF | 0
j27 | r16 | t16 | 0 | 0 | INF | 0
j27 | r16 | t17 | 0 | 21.28 | INF | 0
j27 | r16 | t18 | 0 | 16.89 | INF | 0
j27 | r16 | t19 | 0 | 0 | INF | 0
j27 | r16 | t20 | 0 | 39.5 | INF | 0
j27 | r16 | t21 | 0 | 0 | INF | 0
j27 | r16 | t22 | 0 | 0 | INF | 0
j27 | r16 | t23 | 0 | 13.933 | INF | 0
j27 | r16 | t24 | 0 | 12.897 | INF | 0
j27 | r161 | t1 | 0 | 47.33 | INF | 0
j27 | r161 | t2 | 0 | 105.7586 | INF | 0
j27 | r161 | t3 | 0 | 131.817 | INF | 0
j27 | r161 | t4 | 0 | 0 | INF | 0
j27 | r161 | t5 | 0 | 0.58985 | INF | 0
j27 | r161 | t6 | 0 | 0 | INF | 0
j27 | r161 | t7 | 0 | 109.1741 | INF | 0
j27 | r161 | t8 | 0 | 20.0895 | INF | 0
j27 | r161 | t9 | 0 | 4 | INF | 0
j27 | r161 | t10 | 0 | 42.67 | INF | 0
j27 | r161 | t11 | 0 | 60 | INF | 0
j27 | r161 | t12 | 0 | 0 | INF | 0
j27 | r161 | t13 | 0 | 153.0588 | INF | 0
j27 | r161 | t14 | 0 | 105.1012 | INF | 0
j27 | r161 | t15 | 0 | 55.1744 | INF | 0
j27 | r161 | t16 | 0 | 3.4792 | INF | 0
j27 | r161 | t17 | 0 | 154.7574 | INF | 0
j27 | r161 | t18 | 0 | 0 | INF | 0
j27 | r161 | t19 | 0 | 0 | INF | 0
j27 | r161 | t20 | 0 | 138.2427 | INF | 0
j27 | r161 | t21 | 0 | 15.2573 | INF | 0
j27 | r161 | t22 | 0 | 136.1069 | INF | 0
j27 | r161 | t23 | 0 | 59.6413 | INF | 0
j27 | r161 | t24 | 0 | 66.0819 | INF | 0
j30 | r15 | t1 | 0 | 19 | INF | 0
j30 | r15 | t2 | 0 | 29 | INF | 0
j30 | r15 | t3 | 0 | 0 | INF | 0
j30 | r15 | t4 | 0 | 0 | INF | 0
j30 | r15 | t5 | 0 | 126.2 | INF | 0
j30 | r15 | t6 | 0 | 0.14183 | INF | 0
j30 | r15 | t7 | 0 | 0 | INF | 0
j30 | r15 | t8 | 0 | 18.6882 | INF | 0
j30 | r15 | t9 | 0 | 6 | INF | 0
j30 | r15 | t10 | 0 | 13 | INF | 0
j30 | r15 | t11 | 0 | 3.6097 | INF | 0
j30 | r15 | t12 | 0 | 38.8875 | INF | 0
j30 | r15 | t13 | 0 | 0 | INF | 0
j30 | r15 | t14 | 0 | 58.8172 | INF | 0
j30 | r15 | t15 | 0 | 46.3256 | INF | 0
j30 | r15 | t16 | 0 | 0 | INF | 0
j30 | r15 | t17 | 0 | 0 | INF | 0
j30 | r15 | t18 | 0 | 73 | INF | 0
j30 | r15 | t19 | 0 | 0 | INF | 0
j30 | r15 | t20 | 0 | 0 | INF | 0
j30 | r15 | t21 | 0 | 113.3077 | INF | 0
j30 | r15 | t22 | 0 | 0 | INF | 0
j30 | r15 | t23 | 0 | 0 | INF | 0
j30 | r15 | t24 | 0 | 23.8623 | INF | 0
j30 | r151 | t1 | 0 | 76.5618 | INF | 0
j30 | r151 | t2 | 0 | 10.5541 | INF | 0
j30 | r151 | t3 | 0 | 10.5541 | INF | 0
j30 | r151 | t4 | 0 | 157.3934 | INF | 0
j30 | r151 | t5 | 0 | 0 | INF | 0
j30 | r151 | t6 | 0 | 142.3732 | INF | 0
j30 | r151 | t7 | 0 | 0 | INF | 0
j30 | r151 | t8 | 0 | 95.6063 | INF | 0
j30 | r151 | t9 | 0 | 18 | INF | 0
j30 | r151 | t10 | 0 | 42.17 | INF | 0
j30 | r151 | t11 | 0 | 96 | INF | 0
j30 | r151 | t12 | 0 | 132 | INF | 0
j30 | r151 | t13 | 0 | 0 | INF | 0
j30 | r151 | t14 | 0 | 9.4307 | INF | 0
j30 | r151 | t15 | 0 | 59.106 | INF | 0
j30 | r151 | t16 | 0 | 171.7101 | INF | 0
j30 | r151 | t17 | 0 | 0 | INF | 0
j30 | r151 | t18 | 0 | 86.5698 | INF | 0
j30 | r151 | t19 | 0 | 177.2263 | INF | 0
j30 | r151 | t20 | 0 | 0 | INF | 0
j30 | r151 | t21 | 0 | 49.7103 | INF | 0
j30 | r151 | t22 | 0 | 41.2037 | INF | 0
j30 | r151 | t23 | 0 | 104.0062 | INF | 0
j30 | r151 | t24 | 0 | 72.1638 | INF | 0
j2 | j3 | t1 | 0 | 61.7017 | INF | 0
j2 | j3 | t2 | 0 | 83.087 | INF | 0
j2 | j3 | t3 | 0 | 216.1802 | INF | 0
j2 | j3 | t4 | 0 | 93.4637 | INF | 0
j2 | j3 | t5 | 0 | 0 | INF | 0
j2 | j3 | t6 | 0 | 0.089217 | INF | 0
j2 | j3 | t7 | 0 | 82.3549 | INF | 0
j2 | j3 | t8 | 0 | 89.4883 | INF | 0
j2 | j3 | t9 | 0 | 13.17 | INF | 0
j2 | j3 | t10 | 0 | 34.33 | INF | 0
j2 | j3 | t11 | 0 | 42.67 | INF | 0
j2 | j3 | t12 | 0 | 123 | INF | 0
j2 | j3 | t13 | 0 | 0 | INF | 0
j2 | j3 | t14 | 0 | 74.6861 | INF | 0
j2 | j3 | t15 | 0 | 0 | INF | 0
j2 | j3 | t16 | 0 | 0 | INF | 0
j2 | j3 | t17 | 0 | 177.647 | INF | 0
j2 | j3 | t18 | 0 | 0 | INF | 0
j2 | j3 | t19 | 0 | 8.8632 | INF | 0
j2 | j3 | t20 | 0 | 0 | INF | 0
j2 | j3 | t21 | 0 | 74.2787 | INF | 0
j2 | j3 | t22 | 0 | 0 | INF | 0
j2 | j3 | t23 | 0 | 0 | INF | 0
j2 | j3 | t24 | 0 | 62 | INF | 0
j2 | j6 | t1 | 0 | 336.804 | INF | 0
j2 | j6 | t2 | 0 | 315.8482 | INF | 0
j2 | j6 | t3 | 0 | 182.9015 | INF | 0
j2 | j6 | t4 | 0 | 305.6743 | INF | 0
j2 | j6 | t5 | 0 | 399.2062 | INF | 0
j2 | j6 | t6 | 0 | 395.5212 | INF | 0
j2 | j6 | t7 | 0 | 305.0522 | INF | 0
j2 | j6 | t8 | 0 | 285.6294 | INF | 0
j2 | j6 | t9 | 0 | 121.5 | INF | 0
j2 | j6 | t10 | 0 | 152.33 | INF | 0
j2 | j6 | t11 | 0 | 188.2356 | INF | 0
j2 | j6 | t12 | 0 | 109.62 | INF | 0
j2 | j6 | t13 | 0 | 234.5004 | INF | 0
j2 | j6 | t14 | 0 | 161.2369 | INF | 0
j2 | j6 | t15 | 0 | 237.249 | INF | 0
j2 | j6 | t16 | 0 | 238.3922 | INF | 0
j2 | j6 | t17 | 0 | 61.8831 | INF | 0
j2 | j6 | t18 | 0 | 240.097 | INF | 0
j2 | j6 | t19 | 0 | 232.2621 | INF | 0
j2 | j6 | t20 | 0 | 241.8182 | INF | 0
j2 | j6 | t21 | 0 | 168.2542 | INF | 0
j2 | j6 | t22 | 0 | 241.2384 | INF | 0
j2 | j6 | t23 | 0 | 241.6006 | INF | 0
j2 | j6 | t24 | 0 | 180.1952 | INF | 0
j3 | r17 | t1 | 0 | 51.7017 | INF | 0
j3 | r17 | t2 | 0 | 0 | INF | 0
j3 | r17 | t3 | 0 | 154.0605 | INF | 0
j3 | r17 | t4 | 0 | 12.2148 | INF | 0
j3 | r17 | t5 | 0 | 0 | INF | 0
j3 | r17 | t6 | 0 | 0.089217 | INF | 0
j3 | r17 | t7 | 0 | 0.38811 | INF | 0
j3 | r17 | t8 | 0 | 53.6927 | INF | 0
j3 | r17 | t9 | 0 | 5.67 | INF | 0
j3 | r17 | t10 | 0 | 16.33 | INF | 0
j3 | r17 | t11 | 0 | 42.67 | INF | 0
j3 | r17 | t12 | 0 | 46 | INF | 0
j3 | r17 | t13 | 0 | 0 | INF | 0
j3 | r17 | t14 | 0 | 49.693 | INF | 0
j3 | r17 | t15 | 0 | 0 | INF | 0
j3 | r17 | t16 | 0 | 0 | INF | 0
j3 | r17 | t17 | 0 | 177.647 | INF | 0
j3 | r17 | t18 | 0 | 0 | INF | 0
j3 | r17 | t19 | 0 | 5.2443 | INF | 0
j3 | r17 | t20 | 0 | 0 | INF | 0
j3 | r17 | t21 | 0 | 74.2787 | INF | 0
j3 | r17 | t22 | 0 | 0 | INF | 0
j3 | r17 | t23 | 0 | 0 | INF | 0
j3 | r17 | t24 | 0 | 38 | INF | 0
j3 | r171 | t1 | 0 | 10 | INF | 0
j3 | r171 | t2 | 0 | 83.087 | INF | 0
j3 | r171 | t3 | 0 | 62.1198 | INF | 0
j3 | r171 | t4 | 0 | 81.2489 | INF | 0
j3 | r171 | t5 | 0 | 0 | INF | 0
j3 | r171 | t6 | 0 | 0 | INF | 0
j3 | r171 | t7 | 0 | 81.9668 | INF | 0
j3 | r171 | t8 | 0 | 35.7956 | INF | 0
j3 | r171 | t9 | 0 | 7.5 | INF | 0
j3 | r171 | t10 | 0 | 18 | INF | 0
j3 | r171 | t11 | 0 | 0 | INF | 0
j3 | r171 | t12 | 0 | 77 | INF | 0
j3 | r171 | t13 | 0 | 0 | INF | 0
j3 | r171 | t14 | 0 | 24.9931 | INF | 0
j3 | r171 | t15 | 0 | 0 | INF | 0
j3 | r171 | t16 | 0 | 0 | INF | 0
j3 | r171 | t17 | 0 | 0 | INF | 0
j3 | r171 | t18 | 0 | 0 | INF | 0
j3 | r171 | t19 | 0 | 3.6189 | INF | 0
j3 | r171 | t20 | 0 | 0 | INF | 0
j3 | r171 | t21 | 0 | 0 | INF | 0
j3 | r171 | t22 | 0 | 0 | INF | 0
j3 | r171 | t23 | 0 | 0 | INF | 0
j3 | r171 | t24 | 0 | 24 | INF | 0
j6 | j7 | t1 | 0 | 137.75 | INF | 0
j6 | j7 | t2 | 0 | 67.8471 | INF | 0
j6 | j7 | t3 | 0 | 182.9015 | INF | 0
j6 | j7 | t4 | 0 | 59.4749 | INF | 0
j6 | j7 | t5 | 0 | 164.3434 | INF | 0
j6 | j7 | t6 | 0 | 142.5391 | INF | 0
j6 | j7 | t7 | 0 | 295.8527 | INF | 0
j6 | j7 | t8 | 0 | 187.5683 | INF | 0
j6 | j7 | t9 | 0 | 87 | INF | 0
j6 | j7 | t10 | 0 | 107 | INF | 0
j6 | j7 | t11 | 0 | 188.2356 | INF | 0
j6 | j7 | t12 | 0 | 109.62 | INF | 0
j6 | j7 | t13 | 0 | 177.1704 | INF | 0
j6 | j7 | t14 | 0 | 56.4124 | INF | 0
j6 | j7 | t15 | 0 | 194.0306 | INF | 0
j6 | j7 | t16 | 0 | 0 | INF | 0
j6 | j7 | t17 | 0 | 58.6298 | INF | 0
j6 | j7 | t18 | 0 | 0 | INF | 0
j6 | j7 | t19 | 0 | 120.8783 | INF | 0
j6 | j7 | t20 | 0 | 144.4882 | INF | 0
j6 | j7 | t21 | 0 | 56.1334 | INF | 0
j6 | j7 | t22 | 0 | 137.5684 | INF | 0
j6 | j7 | t23 | 0 | 79.3758 | INF | 0
j6 | j7 | t24 | 0 | 135.92 | INF | 0
j6 | j10 | t1 | 0 | 199.054 | INF | 0
j6 | j10 | t2 | 0 | 248.0012 | INF | 0
j6 | j10 | t3 | 0 | 0 | INF | 0
j6 | j10 | t4 | 0 | 246.1994 | INF | 0
j6 | j10 | t5 | 0 | 234.8628 | INF | 0
j6 | j10 | t6 | 0 | 252.9821 | INF | 0
j6 | j10 | t7 | 0 | 9.1994 | INF | 0
j6 | j10 | t8 | 0 | 98.061 | INF | 0
j6 | j10 | t9 | 0 | 34.5 | INF | 0
j6 | j10 | t10 | 0 | 45.33 | INF | 0
j6 | j10 | t11 | 0 | 0 | INF | 0
j6 | j10 | t12 | 0 | 0 | INF | 0
j6 | j10 | t13 | 0 | 57.33 | INF | 0
j6 | j10 | t14 | 0 | 104.8246 | INF | 0
j6 | j10 | t15 | 0 | 43.2184 | INF | 0
j6 | j10 | t16 | 0 | 238.3922 | INF | 0
j6 | j10 | t17 | 0 | 3.2532 | INF | 0
j6 | j10 | t18 | 0 | 240.097 | INF | 0
j6 | j10 | t19 | 0 | 111.3837 | INF | 0
j6 | j10 | t20 | 0 | 97.33 | INF | 0
j6 | j10 | t21 | 0 | 112.1208 | INF | 0
j6 | j10 | t22 | 0 | 103.67 | INF | 0
j6 | j10 | t23 | 0 | 162.2248 | INF | 0
j6 | j10 | t24 | 0 | 44.2752 | INF | 0
j7 | r19 | t1 | 0 | 60.5 | INF | 0
j7 | r19 | t2 | 0 | 67.8471 | INF | 0
j7 | r19 | t3 | 0 | 182.9015 | INF | 0
j7 | r19 | t4 | 0 | 59.4749 | INF | 0
j7 | r19 | t5 | 0 | 164.3434 | INF | 0
j7 | r19 | t6 | 0 | 0 | INF | 0
j7 | r19 | t7 | 0 | 0 | INF | 0
j7 | r19 | t8 | 0 | 102.1931 | INF | 0
j7 | r19 | t9 | 0 | 43 | INF | 0
j7 | r19 | t10 | 0 | 29 | INF | 0
j7 | r19 | t11 | 0 | 89.5 | INF | 0
j7 | r19 | t12 | 0 | 95.67 | INF | 0
j7 | r19 | t13 | 0 | 94.8255 | INF | 0
j7 | r19 | t14 | 0 | 56.4124 | INF | 0
j7 | r19 | t15 | 0 | 0 | INF | 0
j7 | r19 | t16 | 0 | 0 | INF | 0
j7 | r19 | t17 | 0 | 58.6298 | INF | 0
j7 | r19 | t18 | 0 | 0 | INF | 0
j7 | r19 | t19 | 0 | 120.8783 | INF | 0
j7 | r19 | t20 | 0 | 0.68058 | INF | 0
j7 | r19 | t21 | 0 | 56.1334 | INF | 0
j7 | r19 | t22 | 0 | 121.5115 | INF | 0
j7 | r19 | t23 | 0 | 63.3185 | INF | 0
j7 | r19 | t24 | 0 | 81.67 | INF | 0
j7 | r191 | t1 | 0 | 77.25 | INF | 0
j7 | r191 | t2 | 0 | 0 | INF | 0
j7 | r191 | t3 | 0 | 0 | INF | 0
j7 | r191 | t4 | 0 | 0 | INF | 0
j7 | r191 | t5 | 0 | 0 | INF | 0
j7 | r191 | t6 | 0 | 142.5391 | INF | 0
j7 | r191 | t7 | 0 | 295.8527 | INF | 0
j7 | r191 | t8 | 0 | 85.3752 | INF | 0
j7 | r191 | t9 | 0 | 44 | INF | 0
j7 | r191 | t10 | 0 | 78 | INF | 0
j7 | r191 | t11 | 0 | 98.7356 | INF | 0
j7 | r191 | t12 | 0 | 13.95 | INF | 0
j7 | r191 | t13 | 0 | 82.3449 | INF | 0
j7 | r191 | t14 | 0 | 0 | INF | 0
j7 | r191 | t15 | 0 | 194.0306 | INF | 0
j7 | r191 | t16 | 0 | 0 | INF | 0
j7 | r191 | t17 | 0 | 0 | INF | 0
j7 | r191 | t18 | 0 | 0 | INF | 0
j7 | r191 | t19 | 0 | 0 | INF | 0
j7 | r191 | t20 | 0 | 143.8077 | INF | 0
j7 | r191 | t21 | 0 | 0 | INF | 0
j7 | r191 | t22 | 0 | 16.0569 | INF | 0
j7 | r191 | t23 | 0 | 16.0573 | INF | 0
j7 | r191 | t24 | 0 | 54.25 | INF | 0
j10 | r18 | t1 | 0 | 17.8154 | INF | 0
j10 | r18 | t2 | 0 | 7.0146 | INF | 0
j10 | r18 | t3 | 0 | 0 | INF | 0
j10 | r18 | t4 | 0 | 0 | INF | 0
j10 | r18 | t5 | 0 | 68.1056 | INF | 0
j10 | r18 | t6 | 0 | 61.7479 | INF | 0
j10 | r18 | t7 | 0 | 7.5462 | INF | 0
j10 | r18 | t8 | 0 | 9.5473 | INF | 0
j10 | r18 | t9 | 0 | 11.17 | INF | 0
j10 | r18 | t10 | 0 | 21.83 | INF | 0
j10 | r18 | t11 | 0 | 0 | INF | 0
j10 | r18 | t12 | 0 | 0 | INF | 0
j10 | r18 | t13 | 0 | 0 | INF | 0
j10 | r18 | t14 | 0 | 27.4946 | INF | 0
j10 | r18 | t15 | 0 | 43.2184 | INF | 0
j10 | r18 | t16 | 0 | 0 | INF | 0
j10 | r18 | t17 | 0 | 0 | INF | 0
j10 | r18 | t18 | 0 | 0 | INF | 0
j10 | r18 | t19 | 0 | 0 | INF | 0
j10 | r18 | t20 | 0 | 97.33 | INF | 0
j10 | r18 | t21 | 0 | 0 | INF | 0
j10 | r18 | t22 | 0 | 0 | INF | 0
j10 | r18 | t23 | 0 | 0 | INF | 0
j10 | r18 | t24 | 0 | 0 | INF | 0
j10 | r181 | t1 | 0 | 181.2386 | INF | 0
j10 | r181 | t2 | 0 | 240.9866 | INF | 0
j10 | r181 | t3 | 0 | 0 | INF | 0
j10 | r181 | t4 | 0 | 246.1994 | INF | 0
j10 | r181 | t5 | 0 | 166.7572 | INF | 0
j10 | r181 | t6 | 0 | 191.2342 | INF | 0
j10 | r181 | t7 | 0 | 1.6532 | INF | 0
j10 | r181 | t8 | 0 | 88.5138 | INF | 0
j10 | r181 | t9 | 0 | 23.33 | INF | 0
j10 | r181 | t10 | 0 | 23.5 | INF | 0
j10 | r181 | t11 | 0 | 0 | INF | 0
j10 | r181 | t12 | 0 | 0 | INF | 0
j10 | r181 | t13 | 0 | 57.33 | INF | 0
j10 | r181 | t14 | 0 | 77.33 | INF | 0
j10 | r181 | t15 | 0 | 0 | INF | 0
j10 | r181 | t16 | 0 | 238.3922 | INF | 0
j10 | r181 | t17 | 0 | 3.2532 | INF | 0
j10 | r181 | t18 | 0 | 240.097 | INF | 0
j10 | r181 | t19 | 0 | 111.3837 | INF | 0
j10 | r181 | t20 | 0 | 0 | INF | 0
j10 | r181 | t21 | 0 | 112.1208 | INF | 0
j10 | r181 | t22 | 0 | 103.67 | INF | 0
j10 | r181 | t23 | 0 | 162.2248 | INF | 0
j10 | r181 | t24 | 0 | 44.2752 | INF | 0

## Qpompe
TOC
Qpompe | (variable) | DÃ©bit de la pompe (k) Ã (t)
c | d | t | Lowerbound | Value | Upperbound | Marginal
small | p1 | t1 | 0 | 16.3078 | INF | 0
small | p1 | t2 | 0 | 16.3253 | INF | 0
small | p1 | t3 | 0 | 16.3313 | INF | 0
small | p1 | t4 | 0 | 16.3336 | INF | 0
small | p1 | t5 | 0 | 16.3364 | INF | 0
small | p1 | t6 | 0 | 16.1896 | INF | 0
small | p1 | t7 | 0 | 15.8547 | INF | 0
small | p1 | t8 | 0 | 15.353 | INF | 0
small | p1 | t9 | 0 | 78.9917 | INF | 0
small | p1 | t10 | 0 | 70.6848 | INF | 0
small | p1 | t11 | 0 | 33.7138 | INF | 0
small | p1 | t12 | 0 | 33.9631 | INF | 0
small | p1 | t13 | 0 | 34.2365 | INF | 0
small | p1 | t14 | 0 | 34.4434 | INF | 0
small | p1 | t15 | 0 | 34.6362 | INF | 0
small | p1 | t16 | 0 | 34.8024 | INF | 0
small | p1 | t17 | 0 | 34.9679 | INF | 0
small | p1 | t18 | 0 | 35.0503 | INF | 0
small | p1 | t19 | 0 | 35.1998 | INF | 0
small | p1 | t20 | 0 | 35.3006 | INF | 0
small | p1 | t21 | 0 | 35.4045 | INF | 0
small | p1 | t22 | 0 | 35.2163 | INF | 0
small | p1 | t23 | 0 | 35.2689 | INF | 0
small | p1 | t24 | 0 | 35.3554 | INF | 0
small | p2 | t1 | 0 | 16.3078 | INF | 0
small | p2 | t2 | 0 | 16.3253 | INF | 0
small | p2 | t3 | 0 | 16.3313 | INF | 0
small | p2 | t4 | 0 | 16.3336 | INF | 0
small | p2 | t5 | 0 | 16.3364 | INF | 0
small | p2 | t6 | 0 | 16.1896 | INF | 0
small | p2 | t7 | 0 | 15.8547 | INF | 0
small | p2 | t8 | 0 | 15.353 | INF | 0
small | p2 | t9 | 0 | 78.9917 | INF | 0
small | p2 | t10 | 0 | 70.6848 | INF | 0
small | p2 | t11 | 0 | 33.7138 | INF | 0
small | p2 | t12 | 0 | 33.9631 | INF | 0
small | p2 | t13 | 0 | 34.2365 | INF | 0
small | p2 | t14 | 0 | 34.4434 | INF | 0
small | p2 | t15 | 0 | 34.6362 | INF | 0
small | p2 | t16 | 0 | 34.8024 | INF | 0
small | p2 | t17 | 0 | 34.9679 | INF | 0
small | p2 | t18 | 0 | 35.0503 | INF | 0
small | p2 | t19 | 0 | 35.1998 | INF | 0
small | p2 | t20 | 0 | 35.3006 | INF | 0
small | p2 | t21 | 0 | 35.4045 | INF | 0
small | p2 | t22 | 0 | 35.2163 | INF | 0
small | p2 | t23 | 0 | 35.2689 | INF | 0
small | p2 | t24 | 0 | 35.3554 | INF | 0
large | p1 | t1 | 0 | 266.6279 | INF | 0
large | p1 | t2 | 0 | 266.631 | INF | 0
large | p1 | t3 | 0 | 130.2877 | INF | 0
large | p1 | t4 | 0 | 266.6324 | INF | 0
large | p1 | t5 | 0 | 266.6329 | INF | 0
large | p1 | t6 | 0 | 266.6077 | INF | 0
large | p1 | t7 | 0 | 74.0786 | INF | 0
large | p1 | t8 | 0 | 266.4687 | INF | 0
large | p1 | t9 | 0 | 1 | INF | 0
large | p1 | t10 | 0 | 221.6797 | INF | 0
large | p1 | t11 | 0 | 271.175 | INF | 0
large | p1 | t12 | 0 | 271.2624 | INF | 0
large | p1 | t13 | 0 | 1 | INF | 0
large | p1 | t14 | 0 | 180.6073 | INF | 0
large | p1 | t15 | 0 | 182.7078 | INF | 0
large | p1 | t16 | 0 | 271.561 | INF | 0
large | p1 | t17 | 0 | 271.6207 | INF | 0
large | p1 | t18 | 0 | 147.7486 | INF | 0
large | p1 | t19 | 0 | 195.1487 | INF | 0
large | p1 | t20 | 0 | 271.7415 | INF | 0
large | p1 | t21 | 0 | 69.4552 | INF | 0
large | p1 | t22 | 0 | 271.7108 | INF | 0
large | p1 | t23 | 0 | 271.73 | INF | 0
large | p1 | t24 | 0 | 266.7319 | INF | 0
large | p2 | t1 | 0 | 266.6279 | INF | 0
large | p2 | t2 | 0 | 266.631 | INF | 0
large | p2 | t3 | 0 | 130.2877 | INF | 0
large | p2 | t4 | 0 | 266.6324 | INF | 0
large | p2 | t5 | 0 | 249.8837 | INF | 0
large | p2 | t6 | 0 | 266.6077 | INF | 0
large | p2 | t7 | 0 | 266.5512 | INF | 0
large | p2 | t8 | 0 | 217.8504 | INF | 0
large | p2 | t9 | 0 | 89.1887 | INF | 0
large | p2 | t10 | 0 | 9.7911 | INF | 0
large | p2 | t11 | 0 | 138.7608 | INF | 0
large | p2 | t12 | 0 | 12.4118 | INF | 0
large | p2 | t13 | 0 | 179.8108 | INF | 0
large | p2 | t14 | 0 | 271.4324 | INF | 0
large | p2 | t15 | 0 | 271.5013 | INF | 0
large | p2 | t16 | 0 | 67.7206 | INF | 0
large | p2 | t17 | 0 | 124.4972 | INF | 0
large | p2 | t18 | 0 | 180.355 | INF | 0
large | p2 | t19 | 0 | 267.563 | INF | 0
large | p2 | t20 | 0 | 177.1561 | INF | 0
large | p2 | t21 | 0 | 271.7795 | INF | 0
large | p2 | t22 | 0 | 127.0098 | INF | 0
large | p2 | t23 | 0 | 100.8191 | INF | 0
large | p2 | t24 | 0 | 66.6886 | INF | 0
large | p3 | t1 | 0 | 122.282 | INF | 0
large | p3 | t2 | 0 | 94.1978 | INF | 0
large | p3 | t3 | 0 | 130.2877 | INF | 0
large | p3 | t4 | 0 | 69.5407 | INF | 0
large | p3 | t5 | 0 | 97.6445 | INF | 0
large | p3 | t6 | 0 | 30.5118 | INF | 0
large | p3 | t7 | 0 | 30.9136 | INF | 0
large | p3 | t8 | 0 | 1 | INF | 0
large | p3 | t9 | 0 | 1 | INF | 0
large | p3 | t10 | 0 | 9.7911 | INF | 0
large | p3 | t11 | 0 | 17.4254 | INF | 0
large | p3 | t12 | 0 | 30.1767 | INF | 0
large | p3 | t13 | 0 | 249.5685 | INF | 0
large | p3 | t14 | 0 | 1.5292 | INF | 0
large | p3 | t15 | 0 | 1 | INF | 0
large | p3 | t16 | 0 | 60.0508 | INF | 0
large | p3 | t17 | 0 | 32.7418 | INF | 0
large | p3 | t18 | 0 | 67.3016 | INF | 0
large | p3 | t19 | 0 | 1 | INF | 0
large | p3 | t20 | 0 | 1 | INF | 0
large | p3 | t21 | 0 | 63.1108 | INF | 0
large | p3 | t22 | 0 | 33.1058 | INF | 0
large | p3 | t23 | 0 | 46.5447 | INF | 0
large | p3 | t24 | 0 | 66.6886 | INF | 0
large | p4 | t1 | 0 | 1 | INF | 0
large | p4 | t2 | 0 | 29.7918 | INF | 0
large | p4 | t3 | 0 | 266.6319 | INF | 0
large | p4 | t4 | 0 | 54.783 | INF | 0
large | p4 | t5 | 0 | 43.5408 | INF | 0
large | p4 | t6 | 0 | 87.9994 | INF | 0
large | p4 | t7 | 0 | 266.5512 | INF | 0
large | p4 | t8 | 0 | 132.3535 | INF | 0
large | p4 | t9 | 0 | 1 | INF | 0
large | p4 | t10 | 0 | 9.7911 | INF | 0
large | p4 | t11 | 0 | 17.4254 | INF | 0
large | p4 | t12 | 0 | 134.2783 | INF | 0
large | p4 | t13 | 0 | 21.416 | INF | 0
large | p4 | t14 | 0 | 1 | INF | 0
large | p4 | t15 | 0 | 1.9451 | INF | 0
large | p4 | t16 | 0 | 60.0508 | INF | 0
large | p4 | t17 | 0 | 32.7418 | INF | 0
large | p4 | t18 | 0 | 67.3016 | INF | 0
large | p4 | t19 | 0 | 1 | INF | 0
large | p4 | t20 | 0 | 16.1651 | INF | 0
large | p4 | t21 | 0 | 63.1108 | INF | 0
large | p4 | t22 | 0 | 33.1058 | INF | 0
large | p4 | t23 | 0 | 46.5447 | INF | 0
large | p4 | t24 | 0 | 66.6886 | INF | 0

## Qpompe_inf
TOC
Qpompe_inf | (equation) | Borne infÃ©rieur pompe (k) Ã (t)
c | d | t | Lowerbound | Value | Upperbound | Marginal
small | p1 | t1 | 0 | 15.3078 | INF | 0
small | p1 | t2 | 0 | 15.3253 | INF | 0
small | p1 | t3 | 0 | 15.3313 | INF | 0
small | p1 | t4 | 0 | 15.3336 | INF | 0
small | p1 | t5 | 0 | 15.3364 | INF | 0
small | p1 | t6 | 0 | 15.1896 | INF | 0
small | p1 | t7 | 0 | 14.8547 | INF | 0
small | p1 | t8 | 0 | 14.353 | INF | 0
small | p1 | t9 | 0 | 77.9917 | INF | 0
small | p1 | t10 | 0 | 69.6848 | INF | 0
small | p1 | t11 | 0 | 32.7138 | INF | 0
small | p1 | t12 | 0 | 32.9631 | INF | 0
small | p1 | t13 | 0 | 33.2365 | INF | 0
small | p1 | t14 | 0 | 33.4434 | INF | 0
small | p1 | t15 | 0 | 33.6362 | INF | 0
small | p1 | t16 | 0 | 33.8024 | INF | 0
small | p1 | t17 | 0 | 33.9679 | INF | 0
small | p1 | t18 | 0 | 34.0503 | INF | 0
small | p1 | t19 | 0 | 34.1998 | INF | 0
small | p1 | t20 | 0 | 34.3006 | INF | 0
small | p1 | t21 | 0 | 34.4045 | INF | 0
small | p1 | t22 | 0 | 34.2163 | INF | 0
small | p1 | t23 | 0 | 34.2689 | INF | 0
small | p1 | t24 | 0 | 34.3554 | INF | 0
small | p2 | t1 | 0 | 15.3078 | INF | 0
small | p2 | t2 | 0 | 15.3253 | INF | 0
small | p2 | t3 | 0 | 15.3313 | INF | 0
small | p2 | t4 | 0 | 15.3336 | INF | 0
small | p2 | t5 | 0 | 15.3364 | INF | 0
small | p2 | t6 | 0 | 15.1896 | INF | 0
small | p2 | t7 | 0 | 14.8547 | INF | 0
small | p2 | t8 | 0 | 14.353 | INF | 0
small | p2 | t9 | 0 | 77.9917 | INF | 0
small | p2 | t10 | 0 | 69.6848 | INF | 0
small | p2 | t11 | 0 | 32.7138 | INF | 0
small | p2 | t12 | 0 | 32.9631 | INF | 0
small | p2 | t13 | 0 | 33.2365 | INF | 0
small | p2 | t14 | 0 | 33.4434 | INF | 0
small | p2 | t15 | 0 | 33.6362 | INF | 0
small | p2 | t16 | 0 | 33.8024 | INF | 0
small | p2 | t17 | 0 | 33.9679 | INF | 0
small | p2 | t18 | 0 | 34.0503 | INF | 0
small | p2 | t19 | 0 | 34.1998 | INF | 0
small | p2 | t20 | 0 | 34.3006 | INF | 0
small | p2 | t21 | 0 | 34.4045 | INF | 0
small | p2 | t22 | 0 | 34.2163 | INF | 0
small | p2 | t23 | 0 | 34.2689 | INF | 0
small | p2 | t24 | 0 | 34.3554 | INF | 0
large | p1 | t1 | 0 | 265.6279 | INF | 0
large | p1 | t2 | 0 | 265.631 | INF | 0
large | p1 | t3 | 0 | 129.2877 | INF | 0
large | p1 | t4 | 0 | 265.6324 | INF | 0
large | p1 | t5 | 0 | 265.6329 | INF | 0
large | p1 | t6 | 0 | 265.6077 | INF | 0
large | p1 | t7 | 0 | 73.0786 | INF | 0
large | p1 | t8 | 0 | 265.4687 | INF | 0
large | p1 | t9 | 0 | 0 | INF | 0
large | p1 | t10 | 0 | 220.6797 | INF | 0
large | p1 | t11 | 0 | 270.175 | INF | 0
large | p1 | t12 | 0 | 270.2624 | INF | 0
large | p1 | t13 | 0 | 0 | INF | 0
large | p1 | t14 | 0 | 179.6073 | INF | 0
large | p1 | t15 | 0 | 181.7078 | INF | 0
large | p1 | t16 | 0 | 270.561 | INF | 0
large | p1 | t17 | 0 | 270.6207 | INF | 0
large | p1 | t18 | 0 | 146.7486 | INF | 0
large | p1 | t19 | 0 | 194.1487 | INF | 0
large | p1 | t20 | 0 | 270.7415 | INF | 0
large | p1 | t21 | 0 | 68.4552 | INF | 0
large | p1 | t22 | 0 | 270.7108 | INF | 0
large | p1 | t23 | 0 | 270.73 | INF | 0
large | p1 | t24 | 0 | 265.7319 | INF | 0
large | p2 | t1 | 0 | 265.6279 | INF | 0
large | p2 | t2 | 0 | 265.631 | INF | 0
large | p2 | t3 | 0 | 129.2877 | INF | 0
large | p2 | t4 | 0 | 265.6324 | INF | 0
large | p2 | t5 | 0 | 248.8837 | INF | 0
large | p2 | t6 | 0 | 265.6077 | INF | 0
large | p2 | t7 | 0 | 265.5512 | INF | 0
large | p2 | t8 | 0 | 216.8504 | INF | 0
large | p2 | t9 | 0 | 88.1887 | INF | 0
large | p2 | t10 | 0 | 8.7911 | INF | 0
large | p2 | t11 | 0 | 137.7608 | INF | 0
large | p2 | t12 | 0 | 11.4118 | INF | 0
large | p2 | t13 | 0 | 178.8108 | INF | 0
large | p2 | t14 | 0 | 270.4324 | INF | 0
large | p2 | t15 | 0 | 270.5013 | INF | 0
large | p2 | t16 | 0 | 66.7206 | INF | 0
large | p2 | t17 | 0 | 123.4972 | INF | 0
large | p2 | t18 | 0 | 179.355 | INF | 0
large | p2 | t19 | 0 | 266.563 | INF | 0
large | p2 | t20 | 0 | 176.1561 | INF | 0
large | p2 | t21 | 0 | 270.7795 | INF | 0
large | p2 | t22 | 0 | 126.0098 | INF | 0
large | p2 | t23 | 0 | 99.8191 | INF | 0
large | p2 | t24 | 0 | 65.6886 | INF | 0
large | p3 | t1 | 0 | 121.282 | INF | 0
large | p3 | t2 | 0 | 93.1978 | INF | 0
large | p3 | t3 | 0 | 129.2877 | INF | 0
large | p3 | t4 | 0 | 68.5407 | INF | 0
large | p3 | t5 | 0 | 96.6445 | INF | 0
large | p3 | t6 | 0 | 29.5118 | INF | 0
large | p3 | t7 | 0 | 29.9136 | INF | 0
large | p3 | t8 | 0 | 0 | INF | 0
large | p3 | t9 | 0 | 0 | INF | 0
large | p3 | t10 | 0 | 8.7911 | INF | 0
large | p3 | t11 | 0 | 16.4254 | INF | 0
large | p3 | t12 | 0 | 29.1767 | INF | 0
large | p3 | t13 | 0 | 248.5685 | INF | 0
large | p3 | t14 | 0 | 0.52919 | INF | 0
large | p3 | t15 | 0 | 0 | INF | 0
large | p3 | t16 | 0 | 59.0508 | INF | 0
large | p3 | t17 | 0 | 31.7418 | INF | 0
large | p3 | t18 | 0 | 66.3016 | INF | 0
large | p3 | t19 | 0 | 0 | INF | 0
large | p3 | t20 | 0 | 0 | INF | 0
large | p3 | t21 | 0 | 62.1108 | INF | 0
large | p3 | t22 | 0 | 32.1058 | INF | 0
large | p3 | t23 | 0 | 45.5447 | INF | 0
large | p3 | t24 | 0 | 65.6886 | INF | 0
large | p4 | t1 | 0 | 0 | INF | 0
large | p4 | t2 | 0 | 28.7918 | INF | 0
large | p4 | t3 | 0 | 265.6319 | INF | 0
large | p4 | t4 | 0 | 53.783 | INF | 0
large | p4 | t5 | 0 | 42.5408 | INF | 0
large | p4 | t6 | 0 | 86.9994 | INF | 0
large | p4 | t7 | 0 | 265.5512 | INF | 0
large | p4 | t8 | 0 | 131.3535 | INF | 0
large | p4 | t9 | 0 | 0 | INF | 0
large | p4 | t10 | 0 | 8.7911 | INF | 0
large | p4 | t11 | 0 | 16.4254 | INF | 0
large | p4 | t12 | 0 | 133.2783 | INF | 0
large | p4 | t13 | 0 | 20.416 | INF | 0
large | p4 | t14 | 0 | 0 | INF | 0
large | p4 | t15 | 0 | 0.94507 | INF | 0
large | p4 | t16 | 0 | 59.0508 | INF | 0
large | p4 | t17 | 0 | 31.7418 | INF | 0
large | p4 | t18 | 0 | 66.3016 | INF | 0
large | p4 | t19 | 0 | 0 | INF | 0
large | p4 | t20 | 0 | 15.1651 | INF | 0
large | p4 | t21 | 0 | 62.1108 | INF | 0
large | p4 | t22 | 0 | 32.1058 | INF | 0
large | p4 | t23 | 0 | 45.5447 | INF | 0
large | p4 | t24 | 0 | 65.6886 | INF | 0

## Qpompe_sup
TOC
Qpompe_sup | (equation) | Borne supÃ©rieur pompe (k) Ã (t)
c | d | t | Lowerbound | Value | Upperbound | Marginal
small | p1 | t1 | -INF | -366.5481 | 0 | 0
small | p1 | t2 | -INF | -366.5305 | 0 | 0
small | p1 | t3 | -INF | -366.5245 | 0 | 0
small | p1 | t4 | -INF | -366.5223 | 0 | 0
small | p1 | t5 | -INF | -366.5195 | 0 | 0
small | p1 | t6 | -INF | -366.6663 | 0 | 0
small | p1 | t7 | -INF | -367.0012 | 0 | 0
small | p1 | t8 | -INF | -367.5029 | 0 | 0
small | p1 | t9 | -INF | -303.8642 | 0 | 0
small | p1 | t10 | -INF | -312.1711 | 0 | 0
small | p1 | t11 | -INF | -349.1421 | 0 | 0
small | p1 | t12 | -INF | -348.8928 | 0 | 0
small | p1 | t13 | -INF | -348.6194 | 0 | 0
small | p1 | t14 | -INF | -348.4125 | 0 | 0
small | p1 | t15 | -INF | -348.2197 | 0 | 0
small | p1 | t16 | -INF | -348.0534 | 0 | 0
small | p1 | t17 | -INF | -347.888 | 0 | 0
small | p1 | t18 | -INF | -347.8056 | 0 | 0
small | p1 | t19 | -INF | -347.656 | 0 | 0
small | p1 | t20 | -INF | -347.5553 | 0 | 0
small | p1 | t21 | -INF | -347.4514 | 0 | 0
small | p1 | t22 | -INF | -347.6396 | 0 | 0
small | p1 | t23 | -INF | -347.5869 | 0 | 0
small | p1 | t24 | -INF | -347.5005 | 0 | 0
small | p2 | t1 | -INF | -366.5481 | 0 | 0
small | p2 | t2 | -INF | -366.5305 | 0 | 0
small | p2 | t3 | -INF | -366.5245 | 0 | 0
small | p2 | t4 | -INF | -366.5223 | 0 | 0
small | p2 | t5 | -INF | -366.5195 | 0 | 0
small | p2 | t6 | -INF | -366.6663 | 0 | 0
small | p2 | t7 | -INF | -367.0012 | 0 | 0
small | p2 | t8 | -INF | -367.5029 | 0 | 0
small | p2 | t9 | -INF | -303.8642 | 0 | 0
small | p2 | t10 | -INF | -312.1711 | 0 | 0
small | p2 | t11 | -INF | -349.1421 | 0 | 0
small | p2 | t12 | -INF | -348.8928 | 0 | 0
small | p2 | t13 | -INF | -348.6194 | 0 | 0
small | p2 | t14 | -INF | -348.4125 | 0 | 0
small | p2 | t15 | -INF | -348.2197 | 0 | 0
small | p2 | t16 | -INF | -348.0534 | 0 | 0
small | p2 | t17 | -INF | -347.888 | 0 | 0
small | p2 | t18 | -INF | -347.8056 | 0 | 0
small | p2 | t19 | -INF | -347.656 | 0 | 0
small | p2 | t20 | -INF | -347.5553 | 0 | 0
small | p2 | t21 | -INF | -347.4514 | 0 | 0
small | p2 | t22 | -INF | -347.6396 | 0 | 0
small | p2 | t23 | -INF | -347.5869 | 0 | 0
small | p2 | t24 | -INF | -347.5005 | 0 | 0
large | p1 | t1 | -INF | -427.6568 | 0 | 0
large | p1 | t2 | -INF | -427.6538 | 0 | 0
large | p1 | t3 | -INF | -563.9971 | 0 | 0
large | p1 | t4 | -INF | -427.6524 | 0 | 0
large | p1 | t5 | -INF | -427.6519 | 0 | 0
large | p1 | t6 | -INF | -427.6771 | 0 | 0
large | p1 | t7 | -INF | -620.2062 | 0 | 0
large | p1 | t8 | -INF | -427.8161 | 0 | 0
large | p1 | t9 | -INF | -693.2848 | 0 | 0
large | p1 | t10 | -INF | -472.605 | 0 | 0
large | p1 | t11 | -INF | -423.1098 | 0 | 0
large | p1 | t12 | -INF | -423.0224 | 0 | 0
large | p1 | t13 | -INF | -693.2848 | 0 | 0
large | p1 | t14 | -INF | -513.6774 | 0 | 0
large | p1 | t15 | -INF | -511.577 | 0 | 0
large | p1 | t16 | -INF | -422.7238 | 0 | 0
large | p1 | t17 | -INF | -422.6641 | 0 | 0
large | p1 | t18 | -INF | -546.5361 | 0 | 0
large | p1 | t19 | -INF | -499.136 | 0 | 0
large | p1 | t20 | -INF | -422.5432 | 0 | 0
large | p1 | t21 | -INF | -624.8296 | 0 | 0
large | p1 | t22 | -INF | -422.574 | 0 | 0
large | p1 | t23 | -INF | -422.5548 | 0 | 0
large | p1 | t24 | -INF | -427.5529 | 0 | 0
large | p2 | t1 | -INF | -427.6568 | 0 | 0
large | p2 | t2 | -INF | -427.6538 | 0 | 0
large | p2 | t3 | -INF | -563.9971 | 0 | 0
large | p2 | t4 | -INF | -427.6524 | 0 | 0
large | p2 | t5 | -INF | -444.401 | 0 | 0
large | p2 | t6 | -INF | -427.6771 | 0 | 0
large | p2 | t7 | -INF | -427.7336 | 0 | 0
large | p2 | t8 | -INF | -476.4343 | 0 | 0
large | p2 | t9 | -INF | -605.0961 | 0 | 0
large | p2 | t10 | -INF | -684.4936 | 0 | 0
large | p2 | t11 | -INF | -555.5239 | 0 | 0
large | p2 | t12 | -INF | -681.873 | 0 | 0
large | p2 | t13 | -INF | -514.474 | 0 | 0
large | p2 | t14 | -INF | -422.8524 | 0 | 0
large | p2 | t15 | -INF | -422.7835 | 0 | 0
large | p2 | t16 | -INF | -626.5642 | 0 | 0
large | p2 | t17 | -INF | -569.7876 | 0 | 0
large | p2 | t18 | -INF | -513.9298 | 0 | 0
large | p2 | t19 | -INF | -426.7218 | 0 | 0
large | p2 | t20 | -INF | -517.1287 | 0 | 0
large | p2 | t21 | -INF | -422.5053 | 0 | 0
large | p2 | t22 | -INF | -567.275 | 0 | 0
large | p2 | t23 | -INF | -593.4657 | 0 | 0
large | p2 | t24 | -INF | -627.5962 | 0 | 0
large | p3 | t1 | -INF | -572.0027 | 0 | 0
large | p3 | t2 | -INF | -600.0869 | 0 | 0
large | p3 | t3 | -INF | -563.9971 | 0 | 0
large | p3 | t4 | -INF | -624.7441 | 0 | 0
large | p3 | t5 | -INF | -596.6403 | 0 | 0
large | p3 | t6 | -INF | -663.773 | 0 | 0
large | p3 | t7 | -INF | -663.3712 | 0 | 0
large | p3 | t8 | -INF | -693.2848 | 0 | 0
large | p3 | t9 | -INF | -693.2848 | 0 | 0
large | p3 | t10 | -INF | -684.4936 | 0 | 0
large | p3 | t11 | -INF | -676.8594 | 0 | 0
large | p3 | t12 | -INF | -664.1081 | 0 | 0
large | p3 | t13 | -INF | -444.7163 | 0 | 0
large | p3 | t14 | -INF | -692.7556 | 0 | 0
large | p3 | t15 | -INF | -693.2848 | 0 | 0
large | p3 | t16 | -INF | -634.234 | 0 | 0
large | p3 | t17 | -INF | -661.5429 | 0 | 0
large | p3 | t18 | -INF | -626.9832 | 0 | 0
large | p3 | t19 | -INF | -693.2848 | 0 | 0
large | p3 | t20 | -INF | -693.2848 | 0 | 0
large | p3 | t21 | -INF | -631.174 | 0 | 0
large | p3 | t22 | -INF | -661.1789 | 0 | 0
large | p3 | t23 | -INF | -647.7401 | 0 | 0
large | p3 | t24 | -INF | -627.5962 | 0 | 0
large | p4 | t1 | -INF | -693.2848 | 0 | 0
large | p4 | t2 | -INF | -664.493 | 0 | 0
large | p4 | t3 | -INF | -427.6529 | 0 | 0
large | p4 | t4 | -INF | -639.5018 | 0 | 0
large | p4 | t5 | -INF | -650.744 | 0 | 0
large | p4 | t6 | -INF | -606.2854 | 0 | 0
large | p4 | t7 | -INF | -427.7336 | 0 | 0
large | p4 | t8 | -INF | -561.9313 | 0 | 0
large | p4 | t9 | -INF | -693.2848 | 0 | 0
large | p4 | t10 | -INF | -684.4936 | 0 | 0
large | p4 | t11 | -INF | -676.8594 | 0 | 0
large | p4 | t12 | -INF | -560.0064 | 0 | 0
large | p4 | t13 | -INF | -672.8688 | 0 | 0
large | p4 | t14 | -INF | -693.2848 | 0 | 0
large | p4 | t15 | -INF | -692.3397 | 0 | 0
large | p4 | t16 | -INF | -634.234 | 0 | 0
large | p4 | t17 | -INF | -661.5429 | 0 | 0
large | p4 | t18 | -INF | -626.9832 | 0 | 0
large | p4 | t19 | -INF | -693.2848 | 0 | 0
large | p4 | t20 | -INF | -678.1197 | 0 | 0
large | p4 | t21 | -INF | -631.174 | 0 | 0
large | p4 | t22 | -INF | -661.1789 | 0 | 0
large | p4 | t23 | -INF | -647.7401 | 0 | 0
large | p4 | t24 | -INF | -627.5962 | 0 | 0

## r
TOC
r | (set) | reservoirs
n
r12
r13
r132
r133
r134
r14
r15
r151
r16
r161
r17
r171
r18
r181
r19
r191

## Satisfaction_demande
TOC
Satisfaction_demande | (equation) | Satisfaction de la demande en (r) Ã (t)
r | t | Lowerbound | Value | Upperbound | Marginal
r12 | t1 | 96.83 | 96.83 | 96.83 | -0.0079901
r12 | t2 | -7 | -7 | -7 | -0.0079901
r12 | t3 | -4.33 | -4.33 | -4.33 | -0.0079901
r12 | t4 | -6 | -6 | -6 | -0.0079901
r12 | t5 | -6 | -6 | -6 | -0.0079901
r12 | t6 | -3.67 | -3.67 | -3.67 | -0.0079901
r12 | t7 | -2 | -2 | -2 | -0.0079901
r12 | t8 | -4 | -4 | -4 | -0.0079901
r12 | t9 | -3 | -3 | -3 | -0.011823
r12 | t10 | -9.17 | -9.17 | -9.17 | -0.011887
r12 | t11 | -13 | -13 | -13 | -0.012132
r12 | t12 | -17 | -17 | -17 | -0.012132
r12 | t13 | -21 | -21 | -21 | -0.012132
r12 | t14 | -20.67 | -20.67 | -20.67 | -0.012132
r12 | t15 | -20.17 | -20.17 | -20.17 | -0.012132
r12 | t16 | -18 | -18 | -18 | -0.012132
r12 | t17 | -15.83 | -15.83 | -15.83 | -0.012132
r12 | t18 | -17.17 | -17.17 | -17.17 | -0.012132
r12 | t19 | -13 | -13 | -13 | -0.012132
r12 | t20 | -13.33 | -13.33 | -13.33 | -0.012132
r12 | t21 | -19.5 | -19.5 | -19.5 | -0.012132
r12 | t22 | -24.17 | -24.17 | -24.17 | -0.012132
r12 | t23 | -22 | -22 | -22 | -0.012132
r12 | t24 | -20 | -20 | -20 | -0.012132
r13 | t1 | 37.24 | 37.24 | 37.24 | -0.0088109
r13 | t2 | -1.5 | -1.5 | -1.5 | -0.0088109
r13 | t3 | -1.17 | -1.17 | -1.17 | -0.0088109
r13 | t4 | -1.5 | -1.5 | -1.5 | -0.0088109
r13 | t5 | -1.83 | -1.83 | -1.83 | -0.0088109
r13 | t6 | -1.83 | -1.83 | -1.83 | -0.0088109
r13 | t7 | -1 | -1 | -1 | -0.0088109
r13 | t8 | -1 | -1 | -1 | -0.0088109
r13 | t9 | 0 | 0 | 0 | -0.0088109
r13 | t10 | -3.5 | -3.5 | -3.5 | -0.0088109
r13 | t11 | -2 | -2 | -2 | -0.0088109
r13 | t12 | -3 | -3 | -3 | -0.0088109
r13 | t13 | -4 | -4 | -4 | -0.0088109
r13 | t14 | -3 | -3 | -3 | -0.0088109
r13 | t15 | -3 | -3 | -3 | -0.0088109
r13 | t16 | -3 | -3 | -3 | -0.0088109
r13 | t17 | -2 | -2 | -2 | -0.0088109
r13 | t18 | -3 | -3 | -3 | -0.0088109
r13 | t19 | -2 | -2 | -2 | -0.0088109
r13 | t20 | -2 | -2 | -2 | -0.0088109
r13 | t21 | -4 | -4 | -4 | -0.0088109
r13 | t22 | -3 | -3 | -3 | -0.0088109
r13 | t23 | -3 | -3 | -3 | -0.0088109
r13 | t24 | -3 | -3 | -3 | -0.0088109
r132 | t1 | 214.26 | 214.26 | 214.26 | -0.01018
r132 | t2 | -19.5 | -19.5 | -19.5 | -0.01018
r132 | t3 | -16.83 | -16.83 | -16.83 | -0.01018
r132 | t4 | -7.67 | -7.67 | -7.67 | -0.01018
r132 | t5 | -9 | -9 | -9 | -0.01018
r132 | t6 | -9.67 | -9.67 | -9.67 | -0.01018
r132 | t7 | -5.83 | -5.83 | -5.83 | -0.01018
r132 | t8 | -11.67 | -11.67 | -11.67 | -0.01018
r132 | t9 | -6.5 | -6.5 | -6.5 | -0.012322
r132 | t10 | -17 | -17 | -17 | -0.012498
r132 | t11 | -33.67 | -33.67 | -33.67 | -0.013657
r132 | t12 | -41 | -41 | -41 | -0.013657
r132 | t13 | -48 | -48 | -48 | -0.013657
r132 | t14 | -37.5 | -37.5 | -37.5 | -0.013657
r132 | t15 | -34.67 | -34.67 | -34.67 | -0.013657
r132 | t16 | -35.83 | -35.83 | -35.83 | -0.013657
r132 | t17 | -35 | -35 | -35 | -0.013657
r132 | t18 | -36.33 | -36.33 | -36.33 | -0.013657
r132 | t19 | -29.83 | -29.83 | -29.83 | -0.013657
r132 | t20 | -31.5 | -31.5 | -31.5 | -0.013657
r132 | t21 | -30.83 | -30.83 | -30.83 | -0.013657
r132 | t22 | -37.17 | -37.17 | -37.17 | -0.013657
r132 | t23 | -42.67 | -42.67 | -42.67 | -0.013657
r132 | t24 | -35.33 | -35.33 | -35.33 | -0.013657
r133 | t1 | 180.08 | 180.08 | 180.08 | -0.012089
r133 | t2 | -59.33 | -59.33 | -59.33 | -0.012089
r133 | t3 | -37.33 | -37.33 | -37.33 | -0.012089
r133 | t4 | -31 | -31 | -31 | -0.012089
r133 | t5 | -27 | -27 | -27 | -0.012089
r133 | t6 | -26.33 | -26.33 | -26.33 | -0.012089
r133 | t7 | -27 | -27 | -27 | -0.012089
r133 | t8 | -26.5 | -26.5 | -26.5 | -0.0121
r133 | t9 | -30.67 | -30.67 | -30.67 | -0.012944
r133 | t10 | -45.67 | -45.67 | -45.67 | -0.013128
r133 | t11 | -80.83 | -80.83 | -80.83 | -0.015134
r133 | t12 | -113 | -113 | -113 | -0.015134
r133 | t13 | -131.33 | -131.33 | -131.33 | -0.015134
r133 | t14 | -116 | -116 | -116 | -0.015134
r133 | t15 | -96.33 | -96.33 | -96.33 | -0.015134
r133 | t16 | -75 | -75 | -75 | -0.015134
r133 | t17 | -70 | -70 | -70 | -0.015134
r133 | t18 | -65 | -65 | -65 | -0.015134
r133 | t19 | -54 | -54 | -54 | -0.015134
r133 | t20 | -52 | -52 | -52 | -0.015134
r133 | t21 | -79 | -79 | -79 | -0.015134
r133 | t22 | -120.17 | -120.17 | -120.17 | -0.015134
r133 | t23 | -115 | -115 | -115 | -0.015134
r133 | t24 | -78 | -78 | -78 | -0.015134
r134 | t1 | 433.17 | 433.17 | 433.17 | -0.01231
r134 | t2 | -6.83 | -6.83 | -6.83 | -0.012245
r134 | t3 | -5 | -5 | -5 | -0.012215
r134 | t4 | -4.17 | -4.17 | -4.17 | -0.012201
r134 | t5 | -3 | -3 | -3 | -0.012182
r134 | t6 | -5.5 | -5.5 | -5.5 | -0.012429
r134 | t7 | -2 | -2 | -2 | -0.012679
r134 | t8 | -1 | -1 | -1 | -0.012936
r134 | t9 | -2 | -2 | -2 | -0.0132
r134 | t10 | -6.83 | -6.83 | -6.83 | -0.013281
r134 | t11 | -13 | -13 | -13 | -0.013372
r134 | t12 | -19 | -19 | -19 | -0.013562
r134 | t13 | -21 | -21 | -21 | -0.013751
r134 | t14 | -16 | -16 | -16 | -0.013939
r134 | t15 | -15 | -15 | -15 | -0.014125
r134 | t16 | -13 | -13 | -13 | -0.014311
r134 | t17 | -13 | -13 | -13 | -0.014495
r134 | t18 | -6.5 | -6.5 | -6.5 | -0.014679
r134 | t19 | -11.83 | -11.83 | -11.83 | -0.014862
r134 | t20 | -8 | -8 | -8 | -0.015044
r134 | t21 | -15 | -15 | -15 | -0.015226
r134 | t22 | -20 | -20 | -20 | -0.015406
r134 | t23 | -17 | -17 | -17 | -0.01537
r134 | t24 | -10.67 | -10.67 | -10.67 | -0.015293
r14 | t1 | 68.75 | 68.75 | 68.75 | -0.0082976
r14 | t2 | 0 | 0 | 0 | -0.0082976
r14 | t3 | 0 | 0 | 0 | -0.0082976
r14 | t4 | 0 | 0 | 0 | -0.0082976
r14 | t5 | 0 | 0 | 0 | -0.0082976
r14 | t6 | 0 | 0 | 0 | -0.0082976
r14 | t7 | 0 | 0 | 0 | -0.0082976
r14 | t8 | 0 | 0 | 0 | -0.0082976
r14 | t9 | 0 | 0 | 0 | -0.011866
r14 | t10 | -4 | -4 | -4 | -0.011968
r14 | t11 | -16 | -16 | -16 | -0.012364
r14 | t12 | -14 | -14 | -14 | -0.012364
r14 | t13 | -1 | -1 | -1 | -0.012364
r14 | t14 | -5.25 | -5.25 | -5.25 | -0.012364
r14 | t15 | -3.25 | -3.25 | -3.25 | -0.012364
r14 | t16 | -5 | -5 | -5 | -0.012364
r14 | t17 | 0 | 0 | 0 | -0.012364
r14 | t18 | -2 | -2 | -2 | -0.012364
r14 | t19 | -3 | -3 | -3 | -0.012364
r14 | t20 | 0 | 0 | 0 | -0.012364
r14 | t21 | -4.5 | -4.5 | -4.5 | -0.012364
r14 | t22 | -4.25 | -4.25 | -4.25 | -0.012364
r14 | t23 | 0 | 0 | 0 | -0.012364
r14 | t24 | -4 | -4 | -4 | -0.012364
r15 | t1 | 169 | 169 | 169 | -0.0082976
r15 | t2 | -16 | -16 | -16 | -0.0082976
r15 | t3 | -8 | -8 | -8 | -0.0082976
r15 | t4 | -5 | -5 | -5 | -0.0082976
r15 | t5 | -4 | -4 | -4 | -0.0082976
r15 | t6 | -4.33 | -4.33 | -4.33 | -0.0082976
r15 | t7 | -6.33 | -6.33 | -6.33 | -0.0082976
r15 | t8 | -8.17 | -8.17 | -8.17 | -0.0082976
r15 | t9 | -6 | -6 | -6 | -0.011866
r15 | t10 | -13 | -13 | -13 | -0.011968
r15 | t11 | -34.67 | -34.67 | -34.67 | -0.012364
r15 | t12 | -47 | -47 | -47 | -0.012364
r15 | t13 | -49.17 | -49.17 | -49.17 | -0.012364
r15 | t14 | -42.5 | -42.5 | -42.5 | -0.012364
r15 | t15 | -37 | -37 | -37 | -0.012364
r15 | t16 | -28.17 | -28.17 | -28.17 | -0.012364
r15 | t17 | -31.33 | -31.33 | -31.33 | -0.012364
r15 | t18 | -27 | -27 | -27 | -0.012364
r15 | t19 | -23 | -23 | -23 | -0.012364
r15 | t20 | -23 | -23 | -23 | -0.012364
r15 | t21 | -31 | -31 | -31 | -0.012364
r15 | t22 | -46 | -46 | -46 | -0.012364
r15 | t23 | -36.17 | -36.17 | -36.17 | -0.012364
r15 | t24 | -24 | -24 | -24 | -0.012364
r151 | t1 | 768.76 | 768.76 | 768.76 | -0.0082976
r151 | t2 | -34.67 | -34.67 | -34.67 | -0.0082976
r151 | t3 | -15.33 | -15.33 | -15.33 | -0.0082976
r151 | t4 | -10.67 | -10.67 | -10.67 | -0.0082976
r151 | t5 | -10.83 | -10.83 | -10.83 | -0.0082976
r151 | t6 | -10 | -10 | -10 | -0.0082976
r151 | t7 | -10 | -10 | -10 | -0.0082976
r151 | t8 | -20.33 | -20.33 | -20.33 | -0.0082976
r151 | t9 | -18 | -18 | -18 | -0.011866
r151 | t10 | -42.17 | -42.17 | -42.17 | -0.011968
r151 | t11 | -96 | -96 | -96 | -0.012364
r151 | t12 | -132 | -132 | -132 | -0.012364
r151 | t13 | -140.5 | -140.5 | -140.5 | -0.012364
r151 | t14 | -109 | -109 | -109 | -0.012364
r151 | t15 | -85 | -85 | -85 | -0.012364
r151 | t16 | -82 | -82 | -82 | -0.012364
r151 | t17 | -73 | -73 | -73 | -0.012364
r151 | t18 | -61 | -61 | -61 | -0.012364
r151 | t19 | -58 | -58 | -58 | -0.012364
r151 | t20 | -69 | -69 | -69 | -0.012364
r151 | t21 | -111 | -111 | -111 | -0.012364
r151 | t22 | -140 | -140 | -140 | -0.012364
r151 | t23 | -103 | -103 | -103 | -0.012364
r151 | t24 | -73.17 | -73.17 | -73.17 | -0.012364
r16 | t1 | 99 | 99 | 99 | -0.0082976
r16 | t2 | -12 | -12 | -12 | -0.0082976
r16 | t3 | -10 | -10 | -10 | -0.0082976
r16 | t4 | -5 | -5 | -5 | -0.0082976
r16 | t5 | -2 | -2 | -2 | -0.0082976
r16 | t6 | -1 | -1 | -1 | -0.0082976
r16 | t7 | -2 | -2 | -2 | -0.0082976
r16 | t8 | -2 | -2 | -2 | -0.0082976
r16 | t9 | -2.17 | -2.17 | -2.17 | -0.011866
r16 | t10 | -9.17 | -9.17 | -9.17 | -0.011968
r16 | t11 | -10 | -10 | -10 | -0.012364
r16 | t12 | -12 | -12 | -12 | -0.012364
r16 | t13 | -13.33 | -13.33 | -13.33 | -0.012364
r16 | t14 | -13.33 | -13.33 | -13.33 | -0.012364
r16 | t15 | -14.17 | -14.17 | -14.17 | -0.012364
r16 | t16 | -15 | -15 | -15 | -0.012364
r16 | t17 | -13 | -13 | -13 | -0.012364
r16 | t18 | -12 | -12 | -12 | -0.012364
r16 | t19 | -13.17 | -13.17 | -13.17 | -0.012364
r16 | t20 | -12.33 | -12.33 | -12.33 | -0.012364
r16 | t21 | -13.17 | -13.17 | -13.17 | -0.012364
r16 | t22 | -14 | -14 | -14 | -0.012364
r16 | t23 | -13 | -13 | -13 | -0.012364
r16 | t24 | -13.83 | -13.83 | -13.83 | -0.012364
r161 | t1 | 397.56 | 397.56 | 397.56 | -0.0082976
r161 | t2 | -53 | -53 | -53 | -0.0082976
r161 | t3 | -51.83 | -51.83 | -51.83 | -0.0082976
r161 | t4 | -28 | -28 | -28 | -0.0082976
r161 | t5 | -25 | -25 | -25 | -0.0082976
r161 | t6 | -26.67 | -26.67 | -26.67 | -0.0082976
r161 | t7 | -21.67 | -21.67 | -21.67 | -0.0082976
r161 | t8 | -16.67 | -16.67 | -16.67 | -0.0082976
r161 | t9 | -4 | -4 | -4 | -0.011866
r161 | t10 | -42.67 | -42.67 | -42.67 | -0.011968
r161 | t11 | -60 | -60 | -60 | -0.012364
r161 | t12 | -63 | -63 | -63 | -0.012364
r161 | t13 | -110.83 | -110.83 | -110.83 | -0.012364
r161 | t14 | -84.33 | -84.33 | -84.33 | -0.012364
r161 | t15 | -93 | -93 | -93 | -0.012364
r161 | t16 | -67 | -67 | -67 | -0.012364
r161 | t17 | -73 | -73 | -73 | -0.012364
r161 | t18 | -69 | -69 | -69 | -0.012364
r161 | t19 | -56 | -56 | -56 | -0.012364
r161 | t20 | -64 | -64 | -64 | -0.012364
r161 | t21 | -89.5 | -89.5 | -89.5 | -0.012364
r161 | t22 | -99 | -99 | -99 | -0.012364
r161 | t23 | -95.83 | -95.83 | -95.83 | -0.012364
r161 | t24 | -67 | -67 | -67 | -0.012364
r17 | t1 | 190.3 | 190.3 | 190.3 | -0.0076129
r17 | t2 | -26.33 | -26.33 | -26.33 | -0.0076129
r17 | t3 | -10.83 | -10.83 | -10.83 | -0.0076129
r17 | t4 | -12 | -12 | -12 | -0.0076129
r17 | t5 | -12.17 | -12.17 | -12.17 | -0.0076129
r17 | t6 | -15 | -15 | -15 | -0.0076129
r17 | t7 | -13 | -13 | -13 | -0.0076129
r17 | t8 | -14 | -14 | -14 | -0.0076129
r17 | t9 | -5.67 | -5.67 | -5.67 | -0.011773
r17 | t10 | -16.33 | -16.33 | -16.33 | -0.011789
r17 | t11 | -42.67 | -42.67 | -42.67 | -0.011853
r17 | t12 | -46 | -46 | -46 | -0.011853
r17 | t13 | -56.67 | -56.67 | -56.67 | -0.011853
r17 | t14 | -50.67 | -50.67 | -50.67 | -0.011853
r17 | t15 | -46 | -46 | -46 | -0.011853
r17 | t16 | -40 | -40 | -40 | -0.011853
r17 | t17 | -34 | -34 | -34 | -0.011853
r17 | t18 | -31 | -31 | -31 | -0.011853
r17 | t19 | -30 | -30 | -30 | -0.011853
r17 | t20 | -33 | -33 | -33 | -0.011853
r17 | t21 | -36 | -36 | -36 | -0.011853
r17 | t22 | -48.17 | -48.17 | -48.17 | -0.011853
r17 | t23 | -45 | -45 | -45 | -0.011853
r17 | t24 | -38 | -38 | -38 | -0.011853
r171 | t1 | 246.48 | 246.48 | 246.48 | -0.0076129
r171 | t2 | -18.17 | -18.17 | -18.17 | -0.0076129
r171 | t3 | -13 | -13 | -13 | -0.0076129
r171 | t4 | -7.83 | -7.83 | -7.83 | -0.0076129
r171 | t5 | -4.67 | -4.67 | -4.67 | -0.0076129
r171 | t6 | -11 | -11 | -11 | -0.0076129
r171 | t7 | -6 | -6 | -6 | -0.0076129
r171 | t8 | -6 | -6 | -6 | -0.0076129
r171 | t9 | -7.5 | -7.5 | -7.5 | -0.011773
r171 | t10 | -18 | -18 | -18 | -0.011789
r171 | t11 | -39 | -39 | -39 | -0.011853
r171 | t12 | -38 | -38 | -38 | -0.011853
r171 | t13 | -40 | -40 | -40 | -0.011853
r171 | t14 | -35 | -35 | -35 | -0.011853
r171 | t15 | -33 | -33 | -33 | -0.011853
r171 | t16 | -20 | -20 | -20 | -0.011853
r171 | t17 | -23.83 | -23.83 | -23.83 | -0.011853
r171 | t18 | -31 | -31 | -31 | -0.011853
r171 | t19 | -23 | -23 | -23 | -0.011853
r171 | t20 | -17.33 | -17.33 | -17.33 | -0.011853
r171 | t21 | -26.67 | -26.67 | -26.67 | -0.011853
r171 | t22 | -34.83 | -34.83 | -34.83 | -0.011853
r171 | t23 | -21.5 | -21.5 | -21.5 | -0.011853
r171 | t24 | -24 | -24 | -24 | -0.011853
r18 | t1 | 176.84 | 176.84 | 176.84 | -0.0076129
r18 | t2 | -7.67 | -7.67 | -7.67 | -0.0076129
r18 | t3 | -5.83 | -5.83 | -5.83 | -0.0076129
r18 | t4 | -3 | -3 | -3 | -0.0076129
r18 | t5 | -3.33 | -3.33 | -3.33 | -0.0076129
r18 | t6 | -3 | -3 | -3 | -0.0076129
r18 | t7 | -4.5 | -4.5 | -4.5 | -0.0076129
r18 | t8 | -6.5 | -6.5 | -6.5 | -0.0076129
r18 | t9 | -11.17 | -11.17 | -11.17 | -0.011773
r18 | t10 | -21.83 | -21.83 | -21.83 | -0.011789
r18 | t11 | -26 | -26 | -26 | -0.011853
r18 | t12 | -31 | -31 | -31 | -0.011853
r18 | t13 | -27 | -27 | -27 | -0.011853
r18 | t14 | -24 | -24 | -24 | -0.011853
r18 | t15 | -21 | -21 | -21 | -0.011853
r18 | t16 | -21 | -21 | -21 | -0.011853
r18 | t17 | -16.83 | -16.83 | -16.83 | -0.011853
r18 | t18 | -16.5 | -16.5 | -16.5 | -0.011853
r18 | t19 | -17 | -17 | -17 | -0.011853
r18 | t20 | -18.67 | -18.67 | -18.67 | -0.011853
r18 | t21 | -23.33 | -23.33 | -23.33 | -0.011853
r18 | t22 | -21.33 | -21.33 | -21.33 | -0.011853
r18 | t23 | -19 | -19 | -19 | -0.011853
r18 | t24 | -15 | -15 | -15 | -0.011853
r181 | t1 | 821.56 | 821.56 | 821.56 | -0.0076129
r181 | t2 | -149.33 | -149.33 | -149.33 | -0.0076129
r181 | t3 | -128.67 | -128.67 | -128.67 | -0.0076129
r181 | t4 | -105.83 | -105.83 | -105.83 | -0.0076129
r181 | t5 | -93.33 | -93.33 | -93.33 | -0.0076129
r181 | t6 | -62.5 | -62.5 | -62.5 | -0.0076129
r181 | t7 | -41.5 | -41.5 | -41.5 | -0.0076129
r181 | t8 | -26.83 | -26.83 | -26.83 | -0.0076129
r181 | t9 | -23.33 | -23.33 | -23.33 | -0.011773
r181 | t10 | -23.5 | -23.5 | -23.5 | -0.011789
r181 | t11 | -21 | -21 | -21 | -0.011853
r181 | t12 | -18 | -18 | -18 | -0.011853
r181 | t13 | -18.33 | -18.33 | -18.33 | -0.011853
r181 | t14 | -77.33 | -77.33 | -77.33 | -0.011853
r181 | t15 | -137 | -137 | -137 | -0.011853
r181 | t16 | -212.33 | -212.33 | -212.33 | -0.011853
r181 | t17 | -200.83 | -200.83 | -200.83 | -0.011853
r181 | t18 | -160.17 | -160.17 | -160.17 | -0.011853
r181 | t19 | -131.17 | -131.17 | -131.17 | -0.011853
r181 | t20 | -129 | -129 | -129 | -0.011853
r181 | t21 | -117.67 | -117.67 | -117.67 | -0.011853
r181 | t22 | -103.67 | -103.67 | -103.67 | -0.011853
r181 | t23 | -96.17 | -96.17 | -96.17 | -0.011853
r181 | t24 | -110.33 | -110.33 | -110.33 | -0.011853
r19 | t1 | 1157.5 | 1157.5 | 1157.5 | -0.0076129
r19 | t2 | -58.83 | -58.83 | -58.83 | -0.0076129
r19 | t3 | -51.83 | -51.83 | -51.83 | -0.0076129
r19 | t4 | -39.67 | -39.67 | -39.67 | -0.0076129
r19 | t5 | -31.33 | -31.33 | -31.33 | -0.0076129
r19 | t6 | -33 | -33 | -33 | -0.0076129
r19 | t7 | -24 | -24 | -24 | -0.0076129
r19 | t8 | -31.5 | -31.5 | -31.5 | -0.0076129
r19 | t9 | -43 | -43 | -43 | -0.011773
r19 | t10 | -29 | -29 | -29 | -0.011789
r19 | t11 | -89.5 | -89.5 | -89.5 | -0.011853
r19 | t12 | -95.67 | -95.67 | -95.67 | -0.011853
r19 | t13 | -94.83 | -94.83 | -94.83 | -0.011853
r19 | t14 | -92.67 | -92.67 | -92.67 | -0.011853
r19 | t15 | -83.5 | -83.5 | -83.5 | -0.011853
r19 | t16 | -74.5 | -74.5 | -74.5 | -0.011853
r19 | t17 | -65.83 | -65.83 | -65.83 | -0.011853
r19 | t18 | -70.67 | -70.67 | -70.67 | -0.011853
r19 | t19 | -65.5 | -65.5 | -65.5 | -0.011853
r19 | t20 | -68.33 | -68.33 | -68.33 | -0.011853
r19 | t21 | -78.33 | -78.33 | -78.33 | -0.011853
r19 | t22 | -94.33 | -94.33 | -94.33 | -0.011853
r19 | t23 | -90.5 | -90.5 | -90.5 | -0.011853
r19 | t24 | -81.67 | -81.67 | -81.67 | -0.011853
r191 | t1 | 1127.42 | 1127.42 | 1127.42 | -0.0076129
r191 | t2 | -4.75 | -4.75 | -4.75 | -0.0076129
r191 | t3 | -25.75 | -25.75 | -25.75 | -0.0076129
r191 | t4 | -18 | -18 | -18 | -0.0076129
r191 | t5 | -15 | -15 | -15 | -0.0076129
r191 | t6 | -14 | -14 | -14 | -0.0076129
r191 | t7 | 0 | -2.2737e-13 | 0 | -0.0076129
r191 | t8 | -28.25 | -28.25 | -28.25 | -0.0076129
r191 | t9 | -44 | -44 | -44 | -0.011773
r191 | t10 | -78 | -78 | -78 | -0.011789
r191 | t11 | -122 | -122 | -122 | -0.011853
r191 | t12 | -102 | -102 | -102 | -0.011853
r191 | t13 | -87 | -87 | -87 | -0.011853
r191 | t14 | -81 | -81 | -81 | -0.011853
r191 | t15 | -62 | -62 | -62 | -0.011853
r191 | t16 | -94.75 | -94.75 | -94.75 | -0.011853
r191 | t17 | -71 | -71 | -71 | -0.011853
r191 | t18 | -17 | -17 | -17 | -0.011853
r191 | t19 | -37.75 | -37.75 | -37.75 | -0.011853
r191 | t20 | -99 | -99 | -99 | -0.011853
r191 | t21 | -117.25 | -117.25 | -117.25 | -0.011853
r191 | t22 | -92.75 | -92.75 | -92.75 | -0.011853
r191 | t23 | -63 | -63 | -63 | -0.011853
r191 | t24 | -54.25 | -54.25 | -54.25 | -0.011853

## Son
TOC
Son | (variable) | Statu t de la pompe (k) fonctionne Ã (t)
c | d | t | Lowerbound | Value | Upperbound | Marginal
small | p1 | t1 | 0 | 1 | 1 | 0.13945
small | p1 | t2 | 0 | 1 | 1 | 0.14041
small | p1 | t3 | 0 | 1 | 1 | 0.14074
small | p1 | t4 | 0 | 1 | 1 | 0.14086
small | p1 | t5 | 0 | 1 | 1 | 0.14102
small | p1 | t6 | 0 | 1 | 1 | 0.13294
small | p1 | t7 | 0 | 1 | 1 | 0.11395
small | p1 | t8 | 0 | 1 | 1 | 0.083963
small | p1 | t9 | 0 | 1 | 1 | 1.3396
small | p1 | t10 | 0 | 1 | 1 | 1.3054
small | p1 | t11 | 0 | 1 | 1 | 0.94855
small | p1 | t12 | 0 | 1 | 1 | 0.95356
small | p1 | t13 | 0 | 1 | 1 | 0.95897
small | p1 | t14 | 0 | 1 | 1 | 0.963
small | p1 | t15 | 0 | 1 | 1 | 0.96672
small | p1 | t16 | 0 | 1 | 1 | 0.96989
small | p1 | t17 | 0 | 1 | 1 | 0.97302
small | p1 | t18 | 0 | 1 | 1 | 0.97456
small | p1 | t19 | 0 | 1 | 1 | 0.97735
small | p1 | t20 | 0 | 1 | 1 | 0.97922
small | p1 | t21 | 0 | 1 | 1 | 0.98113
small | p1 | t22 | 0 | 1 | 1 | 0.97766
small | p1 | t23 | 0 | 1 | 1 | 0.97863
small | p1 | t24 | 0 | 1 | 1 | 0.98023
small | p2 | t1 | 0 | 1 | 1 | 0.13945
small | p2 | t2 | 0 | 1 | 1 | 0.14041
small | p2 | t3 | 0 | 1 | 1 | 0.14074
small | p2 | t4 | 0 | 1 | 1 | 0.14086
small | p2 | t5 | 0 | 1 | 1 | 0.14102
small | p2 | t6 | 0 | 1 | 1 | 0.13294
small | p2 | t7 | 0 | 1 | 1 | 0.11395
small | p2 | t8 | 0 | 1 | 1 | 0.083963
small | p2 | t9 | 0 | 1 | 1 | 1.3396
small | p2 | t10 | 0 | 1 | 1 | 1.3054
small | p2 | t11 | 0 | 1 | 1 | 0.94855
small | p2 | t12 | 0 | 1 | 1 | 0.95356
small | p2 | t13 | 0 | 1 | 1 | 0.95897
small | p2 | t14 | 0 | 1 | 1 | 0.963
small | p2 | t15 | 0 | 1 | 1 | 0.96672
small | p2 | t16 | 0 | 1 | 1 | 0.96989
small | p2 | t17 | 0 | 1 | 1 | 0.97302
small | p2 | t18 | 0 | 1 | 1 | 0.97456
small | p2 | t19 | 0 | 1 | 1 | 0.97735
small | p2 | t20 | 0 | 1 | 1 | 0.97922
small | p2 | t21 | 0 | 1 | 1 | 0.98113
small | p2 | t22 | 0 | 1 | 1 | 0.97766
small | p2 | t23 | 0 | 1 | 1 | 0.97863
small | p2 | t24 | 0 | 1 | 1 | 0.98023
small | p3 | t1 | 0 | 0 | 1 | EPS
small | p3 | t2 | 0 | 0 | 1 | EPS
small | p3 | t3 | 0 | 0 | 1 | EPS
small | p3 | t4 | 0 | 0 | 1 | EPS
small | p3 | t5 | 0 | 0 | 1 | EPS
small | p3 | t6 | 0 | 0 | 1 | EPS
small | p3 | t7 | 0 | 0 | 1 | EPS
small | p3 | t8 | 0 | 0 | 1 | EPS
small | p3 | t9 | 0 | 0 | 1 | EPS
small | p3 | t10 | 0 | 0 | 1 | EPS
small | p3 | t11 | 0 | 0 | 1 | EPS
small | p3 | t12 | 0 | 0 | 1 | EPS
small | p3 | t13 | 0 | 0 | 1 | EPS
small | p3 | t14 | 0 | 0 | 1 | EPS
small | p3 | t15 | 0 | 0 | 1 | EPS
small | p3 | t16 | 0 | 0 | 1 | EPS
small | p3 | t17 | 0 | 0 | 1 | EPS
small | p3 | t18 | 0 | 0 | 1 | EPS
small | p3 | t19 | 0 | 0 | 1 | EPS
small | p3 | t20 | 0 | 0 | 1 | EPS
small | p3 | t21 | 0 | 0 | 1 | EPS
small | p3 | t22 | 0 | 0 | 1 | EPS
small | p3 | t23 | 0 | 0 | 1 | EPS
small | p3 | t24 | 0 | 0 | 1 | EPS
large | p1 | t1 | 1 | 1 | 1 | 2.2489
large | p1 | t2 | 1 | 1 | 1 | 2.2489
large | p1 | t3 | 1 | 1 | 1 | 2.2489
large | p1 | t4 | 1 | 1 | 1 | 2.2489
large | p1 | t5 | 1 | 1 | 1 | 2.2489
large | p1 | t6 | 1 | 1 | 1 | 2.2489
large | p1 | t7 | 1 | 1 | 1 | 2.2489
large | p1 | t8 | 1 | 1 | 1 | 2.2489
large | p1 | t9 | 1 | 1 | 1 | 3.5547
large | p1 | t10 | 1 | 1 | 1 | 3.5547
large | p1 | t11 | 1 | 1 | 1 | 3.5547
large | p1 | t12 | 1 | 1 | 1 | 3.5547
large | p1 | t13 | 1 | 1 | 1 | 3.5547
large | p1 | t14 | 1 | 1 | 1 | 3.5547
large | p1 | t15 | 1 | 1 | 1 | 3.5547
large | p1 | t16 | 1 | 1 | 1 | 3.5547
large | p1 | t17 | 1 | 1 | 1 | 3.5547
large | p1 | t18 | 1 | 1 | 1 | 3.5547
large | p1 | t19 | 1 | 1 | 1 | 3.5547
large | p1 | t20 | 1 | 1 | 1 | 3.5547
large | p1 | t21 | 1 | 1 | 1 | 3.5547
large | p1 | t22 | 1 | 1 | 1 | 3.5547
large | p1 | t23 | 1 | 1 | 1 | 3.5547
large | p1 | t24 | 1 | 1 | 1 | 3.5547
large | p2 | t1 | 1 | 1 | 1 | 2.2489
large | p2 | t2 | 1 | 1 | 1 | 2.2489
large | p2 | t3 | 1 | 1 | 1 | 2.2489
large | p2 | t4 | 1 | 1 | 1 | 2.2489
large | p2 | t5 | 1 | 1 | 1 | 2.2489
large | p2 | t6 | 1 | 1 | 1 | 2.2489
large | p2 | t7 | 1 | 1 | 1 | 2.2489
large | p2 | t8 | 1 | 1 | 1 | 2.2489
large | p2 | t9 | 1 | 1 | 1 | 3.5547
large | p2 | t10 | 1 | 1 | 1 | 3.5547
large | p2 | t11 | 1 | 1 | 1 | 3.5547
large | p2 | t12 | 1 | 1 | 1 | 3.5547
large | p2 | t13 | 1 | 1 | 1 | 3.5547
large | p2 | t14 | 1 | 1 | 1 | 3.5547
large | p2 | t15 | 1 | 1 | 1 | 3.5547
large | p2 | t16 | 1 | 1 | 1 | 3.5547
large | p2 | t17 | 1 | 1 | 1 | 3.5547
large | p2 | t18 | 1 | 1 | 1 | 3.5547
large | p2 | t19 | 1 | 1 | 1 | 3.5547
large | p2 | t20 | 1 | 1 | 1 | 3.5547
large | p2 | t21 | 1 | 1 | 1 | 3.5547
large | p2 | t22 | 1 | 1 | 1 | 3.5547
large | p2 | t23 | 1 | 1 | 1 | 3.5547
large | p2 | t24 | 1 | 1 | 1 | 3.5547
large | p3 | t1 | 1 | 1 | 1 | 2.2489
large | p3 | t2 | 1 | 1 | 1 | 2.2489
large | p3 | t3 | 1 | 1 | 1 | 2.2489
large | p3 | t4 | 1 | 1 | 1 | 2.2489
large | p3 | t5 | 1 | 1 | 1 | 2.2489
large | p3 | t6 | 1 | 1 | 1 | 2.2489
large | p3 | t7 | 1 | 1 | 1 | 2.2489
large | p3 | t8 | 1 | 1 | 1 | 2.2489
large | p3 | t9 | 1 | 1 | 1 | 3.5547
large | p3 | t10 | 1 | 1 | 1 | 3.5547
large | p3 | t11 | 1 | 1 | 1 | 3.5547
large | p3 | t12 | 1 | 1 | 1 | 3.5547
large | p3 | t13 | 1 | 1 | 1 | 3.5547
large | p3 | t14 | 1 | 1 | 1 | 3.5547
large | p3 | t15 | 1 | 1 | 1 | 3.5547
large | p3 | t16 | 1 | 1 | 1 | 3.5547
large | p3 | t17 | 1 | 1 | 1 | 3.5547
large | p3 | t18 | 1 | 1 | 1 | 3.5547
large | p3 | t19 | 1 | 1 | 1 | 3.5547
large | p3 | t20 | 1 | 1 | 1 | 3.5547
large | p3 | t21 | 1 | 1 | 1 | 3.5547
large | p3 | t22 | 1 | 1 | 1 | 3.5547
large | p3 | t23 | 1 | 1 | 1 | 3.5547
large | p3 | t24 | 1 | 1 | 1 | 3.5547
large | p4 | t1 | 1 | 1 | 1 | 2.2489
large | p4 | t2 | 1 | 1 | 1 | 2.2489
large | p4 | t3 | 1 | 1 | 1 | 2.2489
large | p4 | t4 | 1 | 1 | 1 | 2.2489
large | p4 | t5 | 1 | 1 | 1 | 2.2489
large | p4 | t6 | 1 | 1 | 1 | 2.2489
large | p4 | t7 | 1 | 1 | 1 | 2.2489
large | p4 | t8 | 1 | 1 | 1 | 2.2489
large | p4 | t9 | 1 | 1 | 1 | 3.5547
large | p4 | t10 | 1 | 1 | 1 | 3.5547
large | p4 | t11 | 1 | 1 | 1 | 3.5547
large | p4 | t12 | 1 | 1 | 1 | 3.5547
large | p4 | t13 | 1 | 1 | 1 | 3.5547
large | p4 | t14 | 1 | 1 | 1 | 3.5547
large | p4 | t15 | 1 | 1 | 1 | 3.5547
large | p4 | t16 | 1 | 1 | 1 | 3.5547
large | p4 | t17 | 1 | 1 | 1 | 3.5547
large | p4 | t18 | 1 | 1 | 1 | 3.5547
large | p4 | t19 | 1 | 1 | 1 | 3.5547
large | p4 | t20 | 1 | 1 | 1 | 3.5547
large | p4 | t21 | 1 | 1 | 1 | 3.5547
large | p4 | t22 | 1 | 1 | 1 | 3.5547
large | p4 | t23 | 1 | 1 | 1 | 3.5547
large | p4 | t24 | 1 | 1 | 1 | 3.5547

## surface
TOC
surface | (parameter) | mean surface of each reservoir (m^2)
r | Value
r12 | 35.5
r13 | 29.286
r132 | 77.143
r133 | 52.5
r134 | 87.059
r14 | 38.889
r15 | 85.455
r151 | 199.13
r16 | 40
r161 | 101.111
r17 | 65.294
r171 | 91.6
r18 | 56.111
r181 | 201.538
r19 | 210
r191 | 278.33

## t
TOC
t | (set) | 1-hour periods
dim1
t1
t2
t3
t4
t5
t6
t7
t8
t9
t10
t11
t12
t13
t14
t15
t16
t17
t18
t19
t20
t21
t22
t23
t24

## tariff
TOC
tariff | (parameter) | electricity tariff
t | Value
t1 | 0.02916
t2 | 0.02916
t3 | 0.02916
t4 | 0.02916
t5 | 0.02916
t6 | 0.02916
t7 | 0.02916
t8 | 0.02916
t9 | 0.04609
t10 | 0.04609
t11 | 0.04609
t12 | 0.04609
t13 | 0.04609
t14 | 0.04609
t15 | 0.04609
t16 | 0.04609
t17 | 0.04609
t18 | 0.04609
t19 | 0.04609
t20 | 0.04609
t21 | 0.04609
t22 | 0.04609
t23 | 0.04609
t24 | 0.04609

## v
TOC
v | (variable) | Volume au rÃ©servoir (r) en (t)
n | t | Lowerbound | Value | Upperbound | Marginal
r12 | t1 | 106.5 | 113.4396 | 195.25 | 0
r12 | t2 | 106.5 | 123.0671 | 195.25 | 0
r12 | t3 | 106.5 | 135.3707 | 195.25 | 0
r12 | t4 | 106.5 | 146.0066 | 195.25 | 0
r12 | t5 | 106.5 | 156.6453 | 195.25 | 0
r12 | t6 | 106.5 | 169.4646 | 195.25 | 0
r12 | t7 | 106.5 | 183.6128 | 195.25 | 0
r12 | t8 | 106.5 | 195.25 | 195.25 | -0.0038331
r12 | t9 | 106.5 | 195.25 | 195.25 | -6.3538e-05
r12 | t10 | 106.5 | 195.25 | 195.25 | -0.00024541
r12 | t11 | 106.5 | 193.7349 | 195.25 | 0
r12 | t12 | 106.5 | 188.3047 | 195.25 | 0
r12 | t13 | 106.5 | 178.9676 | 195.25 | 0
r12 | t14 | 106.5 | 170.0309 | 195.25 | 0
r12 | t15 | 106.5 | 161.66 | 195.25 | 0
r12 | t16 | 106.5 | 155.5156 | 195.25 | 0
r12 | t17 | 106.5 | 151.5976 | 195.25 | 0
r12 | t18 | 106.5 | 146.3677 | 195.25 | 0
r12 | t19 | 106.5 | 145.3587 | 195.25 | 0
r12 | t20 | 106.5 | 144.0541 | 195.25 | 0
r12 | t21 | 106.5 | 136.6148 | 195.25 | 0
r12 | t22 | 106.5 | 124.4414 | 195.25 | 0
r12 | t23 | 106.5 | 114.456 | 195.25 | 0
r12 | t24 | 106.5 | 106.5 | 195.25 | 0.012132
r13 | t1 | 38.07 | 44.1044 | 86.977 | 0
r13 | t2 | 38.07 | 49.4781 | 86.977 | 0
r13 | t3 | 38.07 | 55.185 | 86.977 | 0
r13 | t4 | 38.07 | 60.5631 | 86.977 | 0
r13 | t5 | 38.07 | 65.6126 | 86.977 | 0
r13 | t6 | 38.07 | 70.5846 | 86.977 | 0
r13 | t7 | 38.07 | 76.2098 | 86.977 | 0
r13 | t8 | 38.07 | 81.57 | 86.977 | 0
r13 | t9 | 38.07 | 81.57 | 86.977 | 0
r13 | t10 | 38.07 | 78.07 | 86.977 | 0
r13 | t11 | 38.07 | 76.07 | 86.977 | 0
r13 | t12 | 38.07 | 73.07 | 86.977 | 0
r13 | t13 | 38.07 | 69.07 | 86.977 | 0
r13 | t14 | 38.07 | 66.07 | 86.977 | 0
r13 | t15 | 38.07 | 63.07 | 86.977 | 0
r13 | t16 | 38.07 | 60.07 | 86.977 | 0
r13 | t17 | 38.07 | 58.07 | 86.977 | 0
r13 | t18 | 38.07 | 55.07 | 86.977 | 0
r13 | t19 | 38.07 | 53.07 | 86.977 | 0
r13 | t20 | 38.07 | 51.07 | 86.977 | 0
r13 | t21 | 38.07 | 47.07 | 86.977 | 0
r13 | t22 | 38.07 | 44.07 | 86.977 | 0
r13 | t23 | 38.07 | 41.07 | 86.977 | 0
r13 | t24 | 38.07 | 38.07 | 86.977 | 0.0088109
r132 | t1 | 231.43 | 248.3109 | 403.073 | 0
r132 | t2 | 231.43 | 262.8984 | 403.073 | 0
r132 | t3 | 231.43 | 280.1684 | 403.073 | 0
r132 | t4 | 231.43 | 306.6032 | 403.073 | 0
r132 | t5 | 231.43 | 331.7137 | 403.073 | 0
r132 | t6 | 231.43 | 355.8478 | 403.073 | 0
r132 | t7 | 231.43 | 383.1226 | 403.073 | 0
r132 | t8 | 231.43 | 403.073 | 403.073 | -0.0021428
r132 | t9 | 231.43 | 403.073 | 403.073 | -0.00017524
r132 | t10 | 231.43 | 403.073 | 403.073 | -0.0011599
r132 | t11 | 231.43 | 392.739 | 403.073 | 0
r132 | t12 | 231.43 | 375.2509 | 403.073 | 0
r132 | t13 | 231.43 | 350.9558 | 403.073 | 0
r132 | t14 | 231.43 | 337.3065 | 403.073 | 0
r132 | t15 | 231.43 | 326.6234 | 403.073 | 0
r132 | t16 | 231.43 | 314.8975 | 403.073 | 0
r132 | t17 | 231.43 | 304.1183 | 403.073 | 0
r132 | t18 | 231.43 | 292.0673 | 403.073 | 0
r132 | t19 | 231.43 | 286.6218 | 403.073 | 0
r132 | t20 | 231.43 | 279.5774 | 403.073 | 0
r132 | t21 | 231.43 | 273.2763 | 403.073 | 0
r132 | t22 | 231.43 | 260.5025 | 403.073 | 0
r132 | t23 | 231.43 | 242.2657 | 403.073 | 0
r132 | t24 | 231.43 | 231.43 | 403.073 | 0.013657
r133 | t1 | 236.25 | 245.231 | 421.575 | 0
r133 | t2 | 236.25 | 255.1366 | 421.575 | 0
r133 | t3 | 236.25 | 288.9011 | 421.575 | 0
r133 | t4 | 236.25 | 329.8366 | 421.575 | 0
r133 | t5 | 236.25 | 375.9556 | 421.575 | 0
r133 | t6 | 236.25 | 407.1348 | 421.575 | 0
r133 | t7 | 236.25 | 421.575 | 421.575 | -1.1266e-05
r133 | t8 | 236.25 | 421.575 | 421.575 | -0.00084395
r133 | t9 | 236.25 | 421.575 | 421.575 | -0.00018415
r133 | t10 | 236.25 | 421.575 | 421.575 | -0.0020056
r133 | t11 | 236.25 | 417.623 | 421.575 | 0
r133 | t12 | 236.25 | 382.0892 | 421.575 | 0
r133 | t13 | 236.25 | 328.8706 | 421.575 | 0
r133 | t14 | 236.25 | 291.47 | 421.575 | 0
r133 | t15 | 236.25 | 274.1944 | 421.575 | 0
r133 | t16 | 236.25 | 278.641 | 421.575 | 0
r133 | t17 | 236.25 | 288.478 | 421.575 | 0
r133 | t18 | 236.25 | 303.5095 | 421.575 | 0
r133 | t19 | 236.25 | 329.8939 | 421.575 | 0
r133 | t20 | 236.25 | 358.5159 | 421.575 | 0
r133 | t21 | 236.25 | 355.368 | 421.575 | 0
r133 | t22 | 236.25 | 295.6212 | 421.575 | 0
r133 | t23 | 236.25 | 244.1686 | 421.575 | 0
r133 | t24 | 236.25 | 236.25 | 421.575 | 0.015134
r134 | t1 | 444 | 444 | 651.2 | 0.00031471
r134 | t2 | 444 | 444 | 651.2 | 0.00027873
r134 | t3 | 444 | 444 | 651.2 | 0.00026223
r134 | t4 | 444 | 444 | 651.2 | 0.00026776
r134 | t5 | 444 | 444 | 651.2 | 1.7255e-06
r134 | t6 | 444 | 456.4017 | 651.2 | 0
r134 | t7 | 444 | 486.7573 | 651.2 | 0
r134 | t8 | 444 | 531.0701 | 651.2 | 0
r134 | t9 | 444 | 574.2322 | 651.2 | 0
r134 | t10 | 444 | 590.3148 | 651.2 | 0
r134 | t11 | 444 | 577.3148 | 651.2 | 0
r134 | t12 | 444 | 558.3148 | 651.2 | 0
r134 | t13 | 444 | 537.3148 | 651.2 | 0
r134 | t14 | 444 | 521.3148 | 651.2 | 0
r134 | t15 | 444 | 506.3148 | 651.2 | 0
r134 | t16 | 444 | 493.3148 | 651.2 | 0
r134 | t17 | 444 | 480.3148 | 651.2 | 0
r134 | t18 | 444 | 473.8148 | 651.2 | 0
r134 | t19 | 444 | 461.9848 | 651.2 | 0
r134 | t20 | 444 | 453.9848 | 651.2 | 0
r134 | t21 | 444 | 444 | 651.2 | 1.0467e-06
r134 | t22 | 444 | 444 | 651.2 | 0.00021858
r134 | t23 | 444 | 444 | 651.2 | 0.00025818
r134 | t24 | 444 | 444 | 651.2 | 0.015475
r14 | t1 | 70 | 70 | 115.5 | 0
r14 | t2 | 70 | 70 | 115.5 | 0
r14 | t3 | 70 | 70 | 115.5 | 0
r14 | t4 | 70 | 70 | 115.5 | 0
r14 | t5 | 70 | 90.5797 | 115.5 | 0
r14 | t6 | 70 | 104.0536 | 115.5 | 0
r14 | t7 | 70 | 104.0536 | 115.5 | 0
r14 | t8 | 70 | 115.5 | 115.5 | -0.0035682
r14 | t9 | 70 | 115.5 | 115.5 | -0.00010217
r14 | t10 | 70 | 115.5 | 115.5 | -0.00039582
r14 | t11 | 70 | 99.5 | 115.5 | 0
r14 | t12 | 70 | 85.5 | 115.5 | 0
r14 | t13 | 70 | 84.5 | 115.5 | 0
r14 | t14 | 70 | 79.25 | 115.5 | 0
r14 | t15 | 70 | 89.7313 | 115.5 | 0
r14 | t16 | 70 | 84.7313 | 115.5 | 0
r14 | t17 | 70 | 84.7313 | 115.5 | 0
r14 | t18 | 70 | 82.7313 | 115.5 | 0
r14 | t19 | 70 | 79.7313 | 115.5 | 0
r14 | t20 | 70 | 79.7313 | 115.5 | 0
r14 | t21 | 70 | 75.2313 | 115.5 | 0
r14 | t22 | 70 | 70.9813 | 115.5 | 0
r14 | t23 | 70 | 70.9813 | 115.5 | 0
r14 | t24 | 70 | 70 | 115.5 | 0.012364
r15 | t1 | 188 | 188 | 310.2 | 0
r15 | t2 | 188 | 201 | 310.2 | 0
r15 | t3 | 188 | 193 | 310.2 | 0
r15 | t4 | 188 | 188 | 310.2 | 0
r15 | t5 | 188 | 310.2 | 310.2 | 0
r15 | t6 | 188 | 306.0118 | 310.2 | 0
r15 | t7 | 188 | 299.6818 | 310.2 | 0
r15 | t8 | 188 | 310.2 | 310.2 | -0.0035682
r15 | t9 | 188 | 310.2 | 310.2 | -0.00010217
r15 | t10 | 188 | 310.2 | 310.2 | -0.00039582
r15 | t11 | 188 | 279.1397 | 310.2 | 0
r15 | t12 | 188 | 271.0272 | 310.2 | 0
r15 | t13 | 188 | 221.8572 | 310.2 | 0
r15 | t14 | 188 | 238.1744 | 310.2 | 0
r15 | t15 | 188 | 247.5 | 310.2 | 0
r15 | t16 | 188 | 219.33 | 310.2 | 0
r15 | t17 | 188 | 188 | 310.2 | 0
r15 | t18 | 188 | 234 | 310.2 | 0
r15 | t19 | 188 | 211 | 310.2 | 0
r15 | t20 | 188 | 188 | 310.2 | 0
r15 | t21 | 188 | 270.3077 | 310.2 | 0
r15 | t22 | 188 | 224.3077 | 310.2 | 0
r15 | t23 | 188 | 188.1377 | 310.2 | 0
r15 | t24 | 188 | 188 | 310.2 | 0.012364
r151 | t1 | 816.43 | 845.3218 | 1149.973 | 0
r151 | t2 | 816.43 | 821.2059 | 1149.973 | 0
r151 | t3 | 816.43 | 816.43 | 1149.973 | 0
r151 | t4 | 816.43 | 963.1534 | 1149.973 | 0
r151 | t5 | 816.43 | 952.3234 | 1149.973 | 0
r151 | t6 | 816.43 | 1084.6967 | 1149.973 | 0
r151 | t7 | 816.43 | 1074.6967 | 1149.973 | 0
r151 | t8 | 816.43 | 1149.973 | 1149.973 | -0.0035682
r151 | t9 | 816.43 | 1149.973 | 1149.973 | -0.00010217
r151 | t10 | 816.43 | 1149.973 | 1149.973 | -0.00039582
r151 | t11 | 816.43 | 1149.973 | 1149.973 | 0
r151 | t12 | 816.43 | 1149.973 | 1149.973 | 0
r151 | t13 | 816.43 | 1009.473 | 1149.973 | 0
r151 | t14 | 816.43 | 909.9037 | 1149.973 | 0
r151 | t15 | 816.43 | 884.0097 | 1149.973 | 0
r151 | t16 | 816.43 | 973.7199 | 1149.973 | 0
r151 | t17 | 816.43 | 900.7199 | 1149.973 | 0
r151 | t18 | 816.43 | 926.2897 | 1149.973 | 0
r151 | t19 | 816.43 | 1045.516 | 1149.973 | 0
r151 | t20 | 816.43 | 976.516 | 1149.973 | 0
r151 | t21 | 816.43 | 915.2263 | 1149.973 | 0
r151 | t22 | 816.43 | 816.43 | 1149.973 | 0
r151 | t23 | 816.43 | 817.4362 | 1149.973 | 0
r151 | t24 | 816.43 | 816.43 | 1149.973 | 0.012364
r16 | t1 | 112 | 112 | 160.6 | 0
r16 | t2 | 112 | 112 | 160.6 | 0
r16 | t3 | 112 | 117 | 160.6 | 0
r16 | t4 | 112 | 112 | 160.6 | 0
r16 | t5 | 112 | 120.0511 | 160.6 | 0
r16 | t6 | 112 | 119.0511 | 160.6 | 0
r16 | t7 | 112 | 160.6 | 160.6 | 0
r16 | t8 | 112 | 160.6 | 160.6 | -0.0035682
r16 | t9 | 112 | 160.6 | 160.6 | -0.00010217
r16 | t10 | 112 | 160.6 | 160.6 | -0.00039582
r16 | t11 | 112 | 160.6 | 160.6 | 0
r16 | t12 | 112 | 148.6 | 160.6 | 0
r16 | t13 | 112 | 154.5 | 160.6 | 0
r16 | t14 | 112 | 141.17 | 160.6 | 0
r16 | t15 | 112 | 127 | 160.6 | 0
r16 | t16 | 112 | 112 | 160.6 | 0
r16 | t17 | 112 | 120.28 | 160.6 | 0
r16 | t18 | 112 | 125.17 | 160.6 | 0
r16 | t19 | 112 | 112 | 160.6 | 0
r16 | t20 | 112 | 139.17 | 160.6 | 0
r16 | t21 | 112 | 126 | 160.6 | 0
r16 | t22 | 112 | 112 | 160.6 | 0
r16 | t23 | 112 | 112.933 | 160.6 | 0
r16 | t24 | 112 | 112 | 160.6 | 0.012364
r161 | t1 | 444.89 | 444.89 | 589.479 | 0
r161 | t2 | 444.89 | 497.6486 | 589.479 | 0
r161 | t3 | 444.89 | 577.6356 | 589.479 | 0
r161 | t4 | 444.89 | 549.6356 | 589.479 | 0
r161 | t5 | 444.89 | 525.2254 | 589.479 | 0
r161 | t6 | 444.89 | 498.5554 | 589.479 | 0
r161 | t7 | 444.89 | 586.0595 | 589.479 | 0
r161 | t8 | 444.89 | 589.479 | 589.479 | -0.0035682
r161 | t9 | 444.89 | 589.479 | 589.479 | -0.00010217
r161 | t10 | 444.89 | 589.479 | 589.479 | -0.00039582
r161 | t11 | 444.89 | 589.479 | 589.479 | 0
r161 | t12 | 444.89 | 526.479 | 589.479 | 0
r161 | t13 | 444.89 | 568.7078 | 589.479 | 0
r161 | t14 | 444.89 | 589.479 | 589.479 | 0
r161 | t15 | 444.89 | 551.6534 | 589.479 | 0
r161 | t16 | 444.89 | 488.1326 | 589.479 | 0
r161 | t17 | 444.89 | 569.89 | 589.479 | 0
r161 | t18 | 444.89 | 500.89 | 589.479 | 0
r161 | t19 | 444.89 | 444.89 | 589.479 | 0
r161 | t20 | 444.89 | 519.1327 | 589.479 | 0
r161 | t21 | 444.89 | 444.89 | 589.479 | 0
r161 | t22 | 444.89 | 481.9969 | 589.479 | 0
r161 | t23 | 444.89 | 445.8081 | 589.479 | 0
r161 | t24 | 444.89 | 444.89 | 589.479 | 0.012364
r17 | t1 | 215.47 | 242.0017 | 359.117 | 0
r17 | t2 | 215.47 | 215.6717 | 359.117 | 0
r17 | t3 | 215.47 | 358.9022 | 359.117 | 0
r17 | t4 | 215.47 | 359.117 | 359.117 | 0
r17 | t5 | 215.47 | 346.947 | 359.117 | 0
r17 | t6 | 215.47 | 332.0362 | 359.117 | 0
r17 | t7 | 215.47 | 319.4243 | 359.117 | 0
r17 | t8 | 215.47 | 359.117 | 359.117 | -0.0041599
r17 | t9 | 215.47 | 359.117 | 359.117 | -1.5794e-05
r17 | t10 | 215.47 | 359.117 | 359.117 | -6.431e-05
r17 | t11 | 215.47 | 359.117 | 359.117 | 0
r17 | t12 | 215.47 | 359.117 | 359.117 | 0
r17 | t13 | 215.47 | 302.447 | 359.117 | 0
r17 | t14 | 215.47 | 301.47 | 359.117 | 0
r17 | t15 | 215.47 | 255.47 | 359.117 | 0
r17 | t16 | 215.47 | 215.47 | 359.117 | 0
r17 | t17 | 215.47 | 359.117 | 359.117 | 0
r17 | t18 | 215.47 | 328.117 | 359.117 | 0
r17 | t19 | 215.47 | 303.3613 | 359.117 | 0
r17 | t20 | 215.47 | 270.3613 | 359.117 | 0
r17 | t21 | 215.47 | 308.64 | 359.117 | 0
r17 | t22 | 215.47 | 260.47 | 359.117 | 0
r17 | t23 | 215.47 | 215.47 | 359.117 | 0
r17 | t24 | 215.47 | 215.47 | 359.117 | 0.011853
r171 | t1 | 256.48 | 256.48 | 534.028 | 0
r171 | t2 | 256.48 | 321.397 | 534.028 | 0
r171 | t3 | 256.48 | 370.5167 | 534.028 | 0
r171 | t4 | 256.48 | 443.9356 | 534.028 | 0
r171 | t5 | 256.48 | 439.2656 | 534.028 | 0
r171 | t6 | 256.48 | 428.2656 | 534.028 | 0
r171 | t7 | 256.48 | 504.2324 | 534.028 | 0
r171 | t8 | 256.48 | 534.028 | 534.028 | -0.0041599
r171 | t9 | 256.48 | 534.028 | 534.028 | -1.5794e-05
r171 | t10 | 256.48 | 534.028 | 534.028 | -6.431e-05
r171 | t11 | 256.48 | 495.028 | 534.028 | 0
r171 | t12 | 256.48 | 534.028 | 534.028 | 0
r171 | t13 | 256.48 | 494.028 | 534.028 | 0
r171 | t14 | 256.48 | 484.0211 | 534.028 | 0
r171 | t15 | 256.48 | 451.0211 | 534.028 | 0
r171 | t16 | 256.48 | 431.0211 | 534.028 | 0
r171 | t17 | 256.48 | 407.1911 | 534.028 | 0
r171 | t18 | 256.48 | 376.1911 | 534.028 | 0
r171 | t19 | 256.48 | 356.81 | 534.028 | 0
r171 | t20 | 256.48 | 339.48 | 534.028 | 0
r171 | t21 | 256.48 | 312.81 | 534.028 | 0
r171 | t22 | 256.48 | 277.98 | 534.028 | 0
r171 | t23 | 256.48 | 256.48 | 534.028 | 0
r171 | t24 | 256.48 | 256.48 | 534.028 | 0.011853
r18 | t1 | 185.17 | 194.6554 | 314.787 | 0
r18 | t2 | 185.17 | 194 | 314.787 | 0
r18 | t3 | 185.17 | 188.17 | 314.787 | 0
r18 | t4 | 185.17 | 185.17 | 314.787 | 0
r18 | t5 | 185.17 | 249.9456 | 314.787 | 0
r18 | t6 | 185.17 | 308.6935 | 314.787 | 0
r18 | t7 | 185.17 | 311.7397 | 314.787 | 0
r18 | t8 | 185.17 | 314.787 | 314.787 | -0.0041599
r18 | t9 | 185.17 | 314.787 | 314.787 | -1.5794e-05
r18 | t10 | 185.17 | 314.787 | 314.787 | -6.431e-05
r18 | t11 | 185.17 | 288.787 | 314.787 | 0
r18 | t12 | 185.17 | 257.787 | 314.787 | 0
r18 | t13 | 185.17 | 230.787 | 314.787 | 0
r18 | t14 | 185.17 | 234.2816 | 314.787 | 0
r18 | t15 | 185.17 | 256.5 | 314.787 | 0
r18 | t16 | 185.17 | 235.5 | 314.787 | 0
r18 | t17 | 185.17 | 218.67 | 314.787 | 0
r18 | t18 | 185.17 | 202.17 | 314.787 | 0
r18 | t19 | 185.17 | 185.17 | 314.787 | 0
r18 | t20 | 185.17 | 263.83 | 314.787 | 0
r18 | t21 | 185.17 | 240.5 | 314.787 | 0
r18 | t22 | 185.17 | 219.17 | 314.787 | 0
r18 | t23 | 185.17 | 200.17 | 314.787 | 0
r18 | t24 | 185.17 | 185.17 | 314.787 | 0.011853
r181 | t1 | 947.23 | 1002.7986 | 1330.153 | 0
r181 | t2 | 947.23 | 1094.4552 | 1330.153 | 0
r181 | t3 | 947.23 | 965.7852 | 1330.153 | 0
r181 | t4 | 947.23 | 1106.1546 | 1330.153 | 0
r181 | t5 | 947.23 | 1179.5818 | 1330.153 | 0
r181 | t6 | 947.23 | 1308.316 | 1330.153 | 0
r181 | t7 | 947.23 | 1268.4692 | 1330.153 | 0
r181 | t8 | 947.23 | 1330.153 | 1330.153 | -0.0041599
r181 | t9 | 947.23 | 1330.153 | 1330.153 | -1.5794e-05
r181 | t10 | 947.23 | 1330.153 | 1330.153 | -6.431e-05
r181 | t11 | 947.23 | 1309.153 | 1330.153 | 0
r181 | t12 | 947.23 | 1291.153 | 1330.153 | 0
r181 | t13 | 947.23 | 1330.153 | 1330.153 | 0
r181 | t14 | 947.23 | 1330.153 | 1330.153 | 0
r181 | t15 | 947.23 | 1193.153 | 1330.153 | 0
r181 | t16 | 947.23 | 1219.2152 | 1330.153 | 0
r181 | t17 | 947.23 | 1021.6385 | 1330.153 | 0
r181 | t18 | 947.23 | 1101.5654 | 1330.153 | 0
r181 | t19 | 947.23 | 1081.7792 | 1330.153 | 0
r181 | t20 | 947.23 | 952.7792 | 1330.153 | 0
r181 | t21 | 947.23 | 947.23 | 1330.153 | 0
r181 | t22 | 947.23 | 947.23 | 1330.153 | 0
r181 | t23 | 947.23 | 1013.2848 | 1330.153 | 0
r181 | t24 | 947.23 | 947.23 | 1330.153 | 0.011853
r19 | t1 | 1218 | 1218 | 1524.6 | 0
r19 | t2 | 1218 | 1227.0171 | 1524.6 | 0
r19 | t3 | 1218 | 1358.0886 | 1524.6 | 0
r19 | t4 | 1218 | 1377.8935 | 1524.6 | 0
r19 | t5 | 1218 | 1510.9069 | 1524.6 | 0
r19 | t6 | 1218 | 1477.9069 | 1524.6 | 0
r19 | t7 | 1218 | 1453.9069 | 1524.6 | 0
r19 | t8 | 1218 | 1524.6 | 1524.6 | -0.0041599
r19 | t9 | 1218 | 1524.6 | 1524.6 | -1.5794e-05
r19 | t10 | 1218 | 1524.6 | 1524.6 | -6.431e-05
r19 | t11 | 1218 | 1524.6 | 1524.6 | 0
r19 | t12 | 1218 | 1524.6 | 1524.6 | 0
r19 | t13 | 1218 | 1524.5955 | 1524.6 | 0
r19 | t14 | 1218 | 1488.3379 | 1524.6 | 0
r19 | t15 | 1218 | 1404.8379 | 1524.6 | 0
r19 | t16 | 1218 | 1330.3379 | 1524.6 | 0
r19 | t17 | 1218 | 1323.1377 | 1524.6 | 0
r19 | t18 | 1218 | 1252.4677 | 1524.6 | 0
r19 | t19 | 1218 | 1307.846 | 1524.6 | 0
r19 | t20 | 1218 | 1240.1966 | 1524.6 | 0
r19 | t21 | 1218 | 1218 | 1524.6 | 0
r19 | t22 | 1218 | 1245.1815 | 1524.6 | 0
r19 | t23 | 1218 | 1218 | 1524.6 | 0
r19 | t24 | 1218 | 1218 | 1524.6 | 0.011853
r191 | t1 | 1141.17 | 1204.67 | 1622.687 | 0
r191 | t2 | 1141.17 | 1199.92 | 1622.687 | 0
r191 | t3 | 1141.17 | 1174.17 | 1622.687 | 0
r191 | t4 | 1141.17 | 1156.17 | 1622.687 | 0
r191 | t5 | 1141.17 | 1141.17 | 1622.687 | 0
r191 | t6 | 1141.17 | 1269.7091 | 1622.687 | 0
r191 | t7 | 1141.17 | 1565.5618 | 1622.687 | 0
r191 | t8 | 1141.17 | 1622.687 | 1622.687 | -0.0041599
r191 | t9 | 1141.17 | 1622.687 | 1622.687 | -1.5794e-05
r191 | t10 | 1141.17 | 1622.687 | 1622.687 | -6.431e-05
r191 | t11 | 1141.17 | 1599.4226 | 1622.687 | 0
r191 | t12 | 1141.17 | 1511.3727 | 1622.687 | 0
r191 | t13 | 1141.17 | 1506.7176 | 1622.687 | 0
r191 | t14 | 1141.17 | 1425.7176 | 1622.687 | 0
r191 | t15 | 1141.17 | 1557.7481 | 1622.687 | 0
r191 | t16 | 1141.17 | 1462.9981 | 1622.687 | 0
r191 | t17 | 1141.17 | 1391.9981 | 1622.687 | 0
r191 | t18 | 1141.17 | 1374.9981 | 1622.687 | 0
r191 | t19 | 1141.17 | 1337.2481 | 1622.687 | 0
r191 | t20 | 1141.17 | 1382.0558 | 1622.687 | 0
r191 | t21 | 1141.17 | 1264.8058 | 1622.687 | 0
r191 | t22 | 1141.17 | 1188.1127 | 1622.687 | 0
r191 | t23 | 1141.17 | 1141.17 | 1622.687 | 0
r191 | t24 | 1141.17 | 1141.17 | 1622.687 | 0.011853

## vinit
TOC
vinit | (parameter) | initial volume of each reservoir
r | t | Value
r12 | t1 | 106.5
r13 | t1 | 38.07
r132 | t1 | 231.43
r133 | t1 | 236.25
r134 | t1 | 444
r14 | t1 | 70
r15 | t1 | 188
r151 | t1 | 816.43
r16 | t1 | 112
r161 | t1 | 444.89
r17 | t1 | 215.47
r171 | t1 | 256.48
r18 | t1 | 185.17
r181 | t1 | 947.23
r19 | t1 | 1218
r191 | t1 | 1141.17

## vmax
TOC
vmax | (parameter) | maximal volume of each reservoir (m^3)
r | Value
r12 | 177.5
r13 | 79.07
r132 | 366.43
r133 | 383.25
r134 | 592
r14 | 105
r15 | 282
r151 | 1045.43
r16 | 146
r161 | 535.89
r17 | 326.47
r171 | 485.48
r18 | 286.17
r181 | 1209.23
r19 | 1386
r191 | 1475.17

## vmin
TOC
vmin | (parameter) | minimal volume of each reservoir (m^3)
r | Value
r12 | 106.5
r13 | 38.07
r132 | 231.43
r133 | 236.25
r134 | 444
r14 | 70
r15 | 188
r151 | 816.43
r16 | 112
r161 | 444.89
r17 | 215.47
r171 | 256.48
r18 | 185.17
r181 | 947.23
r19 | 1218
r191 | 1141.17